## Capex Projects
UEDCL 2026 CAPEX
Category | Task Name | Region | Scope | Reviewer | Project Status | Remarks
Growth & Access | Connections through the access framework | various
Growth & Access | Connection of 6,100 one pole customers | various
Growth & Access | Transformer Injections | various | 396 Overloaded DTx 71 Overstretched DTs | Enos, Job, Humphrey | At Scoping | Split into Priority 1 (Central)-168 and Priority 2 (Upcountry)-299
Growth & Access | Kigo Substation | Central | a) Split Kampala South – Kigo 11kV feeder at Jeni farm and at St. Phillip C.O.U to create Kigo – Kiranda 11kV and Kigo – Busabala 11kV feeders respectively b) Construct a 33/11kV combined structure to the Kigo area c) Establish 1x15/20 MVA 33/11kV substation at Kigo d) Split Kampala South – Kigo 11kV feeder at Jeni farm and at St. Phillip C.O.U to create Kigo – Kiranda 11kV and Kigo – Busabala 11kV feeders respectively e) Mesh Kampala South – Kigo and Lubowa – Kigo at Kigo Lake view and split Lubowa – Kigo 11kV feeder at Lubugumu TC, and mesh with Kajjansi – Lubowa at Mazolidi towards Kitende to create Kigo – Kitende 11kV feeder f) Split Lubowa – Kigo at Ndejje Lubugumu, mesh with Lubowa – Ndejje at Masitoowa and split at Water pump booster to create Kigo – Ndejje 11kV feeder g) Mesh Lubowa – Kigo 11kV and Kajjansi – Lubowa at Juka and Mild May to create Lubowa – Bunamwaya 11kV feeder | Humphrey | At Scoping | EPC document preparation
Growth & Access | Kabaale UETCL Integration (Kabalega) | Western | Splitting the Hoima – Munteme 33kV feeder: a) Construct a 33 kV feeder bay and gantry at Kabaale UETCL substation on condition that UNOC utilizes all the 33 kV bays. b) Construct an underground cable XLPE 185 sqmm route length 0.3 km to exit the substation to the takeoff structure c) Construct a wooden pole MV line of conductor ACSR 100 sqmm, route length, 2 km | Enos | At Costing | Switching station was deffered. Approved scope to be progressed in 2 phases i.e. refurb & integration; the latter is dependent on UETCL's response on the bay request and or ERA's no objection for an increase in cost as a result of increase in cable scope
|  |  | Network Refurbishment of the Hoima – Munteme 33kV feeder: a) Construct an MV line of conductor ACSR 100 sqmm, route length, 1.52 km b) Replace rotten poles with 157 poles c) Replace LBS with auto reclosers for isolation on fault |  | At Costing
Growth & Access | Mubende Reliability and Load Management plan | Western | Mubende Substation Upgrade: Construction of an indoor substation at Mubende, and upgrade the substation’s transformation capacity by installation of a new 5MVA 33/11kV transformer from Hoima Substation and maintaining the existing 2.5MVA transformer. |  | At Costing
|  |  | Mubende Town Feeder Backbone Conductor Upgrade: Decommission and upgrade a total route length of 17.6 km of conductors from ACSR 25 to ACSR 100 (Mubende substation to Aponye T-off (4.1 km), and from the main T-off to Buganda Tea Factory, Katoma NWSC, and Kaweri T-offs. (13.5 km) Mubende Town Feeder Reconfiguration: Construct a total route length of 0.56 km line segment to break into the existing Mubende 11kV Town feeder to establish a second outgoing 11kV line from Mubende substation. | Job | Document Review
|  |  | Nkonge - Mubende 33kV Feeder reliability improvement: Install two in-line motorized air-break switches, each paired with two auto-Reclosers: one set between Kilume Trading Center T - off and Mile 16 T - off, and another between Lusalira Trading Center T - off and Mile 16 T – off followed by replacement of rotten, Hollow and damaged poles along the feeder |  | At Drawing
Growth & Access | Busunju Substation Capacity Upgrade and Redesign | Central | a) Construct a plant/control house at the substation to house the switch gear, metering equipment, DC Systems, Biometric Substation access control system and SCADA Systems and with a layout that takes into consideration the optimum arrangement of panels to make operations easy. b) Supply, Install, test and commission new indoor GIS switch gear for the 33kV and 11kV feeders to allow protection, switching and isolation in case of system faults, during maintenance or other periods when total deenergization is required. c) Install AC and DC auxiliary systems (auxiliary supply bays/panels, auxiliary transformers, and battery/charger systems, d) Supply, install, test and commission SCADA systems for the new switchgears acquired. e) Lay underground circuits to improve the substation’s appearance and decongest the substation to create space for new equipment installation. f) Decommission and recover 5MVA 33kV/11kV power transformer and 5MVA 33kV autotransformer. g) Decommission and recovery of 33kV and 11kV outdoor switchgear system h) Procure and install a 15/20 MVA 33kV/11kV power transformer | Job | At Costing | 1. UEDCL to procure a 15/20MVA transformer instead of a 10/14MVA for the upgrade of Busunju substation 2. Kireka substation-Pending land acquisition
Growth & Access | Kireka Substation Capacity Upgrade and Redesign | Central | a) Construct a new plant/control house at the substation to house 11kV indoor bus extension, the switch gear, metering equipment, DC Systems, Biometric Substation access control system and SCADA Systems and with a layout that takes into consideration the optimum arrangement of panels to make operations easy. b) Supply, Install, test and commission new indoor GIS switch gear for the 33kV and 11kV feeders to allow protection, switching and isolation in case of system faults, during maintenance or other periods when total deenergization is required. c) Install AC and DC auxiliary systems (auxiliary supply bays/panels, auxiliary transformers, and battery/charger systems d) Supply, install, test and commission SCADA systems for the new switchgears acquired. e) Decommission and recover 2x10/14 MVA 33/11kV power transformers f) Decommission and recovery of 33kV and 11kV indoor switchgear system g) Procure and install 2x15/20 MVA 33kV/11kV power transformers |  | At Costing | UEDCL to fast-track the implementation of the phase 1 line works associated with Nantabulirwa substation as they shall provide relief to the Kireka substation transfomers.
Growth & Access | Kakiri Capacity Enhancement Phase II | Central | Substation scope: a) Construct plant house at Kakiri substation and extend 33kV and 11kV buses. b) Procure and install 6 x 33kV line feeder bays and 6 x 11kV line feeder bays at Kakiri substation. c) Install 1x 3.9MVar 33kV capacitor bank at Kakiri substation |  | At Costing | The justification for installation of a capacitor bank was not included in the submission and was not considered in the review by the regulator
|  |  | Lines scope: c) Construct 33kV feeder of route length 1km XLPE300sqmm single core cable and AAAC 200sqmm 20km wooden pole-mounted and 7km concrete construction line from Namungoona substation to Kakiri substation. d) Construct 33kV feeder line 11km long with a 10km stretch of AAAC 200sqmm and 1km of XLPE 300sqmm substation take-off and cable sections from Namungoona substation to the existing Kawanda-Kakiri 33kV feeder. e) Upgrade 11km of the AAAC150sqm Kawanda-Kakiri feeder portion from the new leg interception point to Kakiri substation to AAAC200sqmm conductor. f) Procure and install 3 x 33kV motorised air-break switches on each feeder leg for switching purposes. | Job | At Drawing
Growth & Access | Luzira substation phase II: UETCL Kitintale 11kV Feeder Uprate | Central | a) Convert 59 transformers on Kitintale feeder and Bugoloobi 11 kV feeders from 11 kV to 33 kV. b) Upgrade 2km of conductor size along feeder backbone from AAAC 100 to AAAC 150. c) Installation of new 33 kV line hardware (insulators, crossarms, line switches). d) Upgrade of protection (circuit breakers, relays, auto-reclosers) to 33 kV class. e) Re-termination of service connections. f) Integration with Luzira 132/33 kV substation. g) Integration with Luzira Industrial 1 33 kV feeder from Luzira UETCL Substation. h) Reinforcement of line supports. | Enos | At Drawing | UEDCL needs to submit an impact assessment of the proposed solutions and an outage management plan for the proposed solution
Growth & Access | Luwero-Kikyusa Area Load and Quality of Supply improvementv Concept | Northern | Install a second transformer at Lumpewe. This transformer will be transferred from Masaka Central Substation to Lumpewe. | Joseph | At Costing | Upgrade works alone were approved
Growth & Access | Kamuli - Namasagali 11kV Feeder Conductor Upgrade | Eastern | a) Decommissioning and upgrading an overall route length of 2.5 km on the backbone conductor from ACSR 25sqmm to ACSR 100sqmm b) Installing a 2MVAr capacitor bank | Job | Document Review
Growth & Access | Integration of Kisoro District to the National Grid | Western | a) Construct a 3-way RMU switching station at Kahengyere b) Construct an insulated MV line ACSR 100 (R/L 18 km) from the switching station to interlink with the Rwanda – Kisoro 30 kV feeder at Kanaaba village c) Construct a new 33 kV line XLPE 185 sqmm (R/L 0.3 km) to integrate the feeders into the RMU d) Install 2*33 kV motorized air-break switches; one at Hakyapa and another one at Kyuho | Joseph | At Drawing | The Authority's approval is subject to submission of an impact assessment of the proposed scope and the cost benefit analysis.
Growth & Access | Mbale Substation Refurbishment | Eastern | Mbale Substation: a) Construct a plant/control house at the substation to house the switch gear, metering equipment, DC Systems, Biometric Substation access control system and SCADA Systems and with a layout that takes into consideration the optimum arrangement of panels to make operations easy. Civils with consideration for flood water management b) Supply, install, test and commission new indoor GIS/Air set switch gear for the 33kV and 11kV feeders to allow protection, switching and isolation in case of system faults, during maintenance or other periods when total deenergization is required. A). 9x33kV Bays i. Four (4) 33kV Feeder Bays ii. One (1) 33kV Buscoupler Bay iii. One (1) Bus Riser Bay iv. 1 Auxiliary Transformer Bay v. Two (2) 33kV Transformer Breaker Bay B) 8 11kV Switchgear vii. Four (4) 11kV Feeder bays viii. Two (2) 11kV Transformer Bays ix. One (1) 11kV Buscoupler Bay x. One (1) 11kV Bus Riser Bay c) Install AC and DC auxiliary systems (auxiliary supply bays/panels, auxiliary transformer and battery/charger systems d) Supply, install, test and commission SCADA systems for the new switchgears acquired e) Supply, installation, test and commission fire Suppression systems f) Lay Underground circuits to improve the substation's appearance and decongest the substation to create space for new equipment installation. |  | Document Review
Asset Replacement & Management | Jinja Industrial Substation Refurbishment | Eastern | a) Construct a plant/control house at the substation to house the switch gear, metering equipment, DC Systems, Biometric Substation access control system and SCADA Systems and with a layout that takes into consideration the optimum arrangement of panels to make operations easy. Civils with consideration for flood water management b) Supply, install, test and commission new indoor GIS/Air set switch gear for the 33kV and 11kV feeders to allow protection, switching and isolation in case of system faults, during maintenance or other periods when total de-energization is required; A) 14 33kV Bays i. Eleven (11) 33kV Feeder Bays ii. Two (2) 33kV Bus coupler Bay iii. One (1) Bus Riser Bay B) 10 11kV Switchgear i. Five (5) 11kV Feeder bays ii. Two (2) 11kV Transformer Bays iii. One (1) 11kV Bus coupler Bay iv. One (1) 11kV Bus Riser Bay c) Install AC and DC auxiliary systems (auxiliary supply bays/panels, auxiliary transformer and battery/charger systems d) Supply, install, test and commission SCADA systems for the new switchgears acquired. e) Supply, installation, test and commission fire Suppression systems f) Lay Underground circuits to improve the substation's appearance and decongest the substation to create space for new equipment installation. | Enos | Document Review
Asset Replacement & Management | Kabale 33/11 kV substation Refurbishment | Western | a) Construct a plant/control house at the substation to house the switch gear, metering equipment, DC Systems, Biometric Substation access control system and SCADA Systems and with a layout that takes into consideration the optimum arrangement of panels to make operations easy. Civils with consideration for flood water management b) Supply, Install, test and commission new indoor GIS switchgear for the 33kV and 11kV feeders to allow protection, switching and isolation in case of system faults, during maintenance or other periods when total deenergization is required. i). 33kV Bays (7): Three (3) 33kV Feeder Bays, One (1) Auxiliary Transformer Bay, One (1) 33kV Transformer Bay, One (1) bus coupler bay and (1) spare Bay. ii). 11kV Switchgear: Three (03) 11kV Feeder bays: One (01) 11kV Transformer Bays plus One (1) spare bay. c) Install AC and DC auxiliary systems (auxiliary supply bays/panels, auxiliary transformer and battery/charger systems, d) Supply, install, test and commission SCADA systems for the new switchgears acquired. e) Supply, installation, test and commission fire suppression systems f) Lay Underground circuits to improve the substation appearance and decongest the substation to create space for new equipment installation. | Enos | Document Review | ERA did not approve the following; 1. Temporary works-20k 2. Decommission of existing assets-30k 3. Installation testing & commissioning-150k 4. External works (Access road, drainage, yard surfacing & fencing)-116k 5. Preliminaries (site preparation)-10k 6. ESIA-10k 7. Detailed design, survey studies, Geotechnical & soil sensitivity tests-5k
Asset Replacement & Management | DC supply system refurbishment for substations | various |  | Humphrey | Documents submitted
Asset Replacement & Management | Procure and Install Distance Relays (15 Pieces), Overcurrent Relays (20 Pieces), Differential Relays for Power Transformers (10 Pieces) | various |  | Humphrey | Documents submitted
Asset Replacement & Management | Procure and install AVR Relay for Power Transformers (10 Pieces) | various |  | Humphrey | Documents submitted
Asset Replacement & Management | Land Asset Protection and Fencing Project | various |  |  | Document Review
Supplementary Capex 7 2025 | Gulu 2, Adjumani Moyo 33kV Feeder interconnection | Northern |  |  | Documents submitted
Supplementary Capex 7 2025 | Kabogere Coffee Factory Transformer Upgrade | Western |  |  | Documents submitted
Supplementary Capex 7 2025 | Kanoni Town Council Relief injection | Western |  |  | Documents submitted
Supplementary Capex 7 2025 | Kapeeka Busunju Feeder integration | Western |  |  | Already implemented | Progressed as E-capex
Supplementary Capex 1 2026 | Kigo Lunnya- Wakiso | Central |  |  | Document Review
Supplementary Capex 8 2025 | Birara Cell, Kisoro | Western |  |  | Documents submitted
Supplementary Capex 8 2025 | Busyechira Village, Busia | Eastern |  |  | Documents submitted
Supplementary Capex 8 2025 | Dure Trading Centre, Pader | Northern |  |  | Documents submitted
Supplementary Capex 8 2025 | Hamutora Centre, Kisoro | Western |  |  | Documents submitted
Supplementary Capex 8 2025 | Kitonya Village, Kasanda | Western |  |  | Documents submitted
Supplementary Capex 8 2025 | Kotia Primary School, Bukedea | Eastern |  |  | Documents submitted
Supplementary Capex 8 2025 | Lwabagabo Ward A, Mubende | Western |  |  | Documents submitted
Supplementary Capex 8 2025 | Mpanga Village, Kakumiro | Northern |  |  | Documents submitted
Supplementary Capex 8 2025 | Ntungamo Centre, Kisoro | Western |  |  | Documents submitted
Supplementary Capex 8 2025 | Porogali Trading Centre, Pader | Northern |  |  | Documents submitted
Supplementary Capex App_One_2025 | Bukasa Bugiri | Eastern |  |  | Documents submitted
Supplementary Capex App_One_2025 | Kawuku Jomayi transformer injection for Bwerenga | Central |  |  | Documents submitted
Supplementary Capex App_One_2025 | Kiwulwe-Kiso transformer injection | Central |  |  | Documents submitted
Supplementary Capex App_One_2025 | Line refurbishment of Laminadera t-off | Northern |  |  | Documents submitted | ERA excluded costs typical of O&M from the final amount
Supplementary Capex App_One_2025 | Nakuwadde T-off Conductor Upgrade | Central |  |  | Documents submitted
Supplementary Capex App_One_2025 | Network Reconfiguration at Akworo Tecwa North |  |  |  |  | ERA rejected Project citing O&M nature
Supplementary Capex App_One_2025 | Reliability of Supply Improvement to Busoga Kingdom and Kivubuka TC | Eastern |  |  | Documents submitted

## TX Injections
No. | Location Name | Region | Feeder Name | Scope for the proposed intervention | Project Status | Remarks | District/Area Office
1 | Nsekwa Village | Central | Wakiso | Inject 100kVA Tx, Construct O/H MV ACSR50 800m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=500m | At Scoping |  | Nakulabye
2 | ZIRU TC | Central | SISSA 11 Kv | Inject 100kVA, extend MV by 300m and LV by 400m | At Drawing |  | ENTEBBE
3 | KAKINDU VILLAGE NO.2 | Central | KAWUKU | Inject 100kVA, MV (500m) and refurblish the existing LV network 500 meters RL | At Drawing |  | ENTEBBE
4 | Kiwangala TC | Western | RAKAI | Upgrade from 50kVA/33kV to 100kv/33kv, Construct O/H MVACSR50 R/L=400M and inject existing 50KVA/33KV transformer, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=400m | At Scoping |  | Masaka
5 | KYOTERA TOWN | Western | RAKAI | Injection of 315KVA/33KV, Extend MV line R/L 300m and reinforcement of the LV network R/L 500m with ACSR50sqmm. | At Scoping |  | SANJE
6 | St Joseph of Nazareth | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MV ACSR50 450m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=400m | At Drawing |  | Natete
7 | Nakyelongosa Tc Booster No.1 | Central | Kiziba | Inject 1x50kVA Tx, Construct O/H MV ACSR50 800m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=500m | At Scoping |  | Nakulabye
8 | KATABI CANAAN SITES REGENCY | Central | KITALA | Upgrading 200kVA, re-inforce 500m of 1phase to 3phase | At Drawing |  | ENTEBBE
9 | Birongo Kitiko No.1 | Central | kigo | Iupgrade to 200Kva tx, re-inforce 1phase LVACSR50 to 3phase | At Drawing |  | Najjanankumbi
10 | Ndejje lunnya | Central | ndejje | Iupgrade to 200Kva tx, re-inforce 1phase LVACSR50 to 3phase | At Drawing |  | Najjanankumbi
11 | Ssekiwunga Village | Central | Kisubi 33KV | Upgrade to 200Kva tx, re-inforce 400m of 1phase LVACSR50 to 3phase and loadcenter the tx | At Drawing |  | Najjanankumbi
12 | St phillip Gangu | Central | kigo | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=450m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=650m | At Drawing |  | Najjanankumbi
13 | Kaazi Atc mast | Central | kigo | upgrade to 200kva tx, re-inforce 1phase LVACSR50 to 3phase of 800m | At Drawing |  | Najjanankumbi
14 | KASALIRWE NASSE | Central | KAPEKA 33KV | injection of 100kVA, RL-HV(1000mts) and RL Lv (800mts) | At Scoping |  | GAYAZA MAGIGYE
15 | MUKONO PARENTS | Central | BUKERERE 11KV | Upgrade 50kVA to 100kVA and re inforcethe existing 1 phase circuit with a 3 phase circuit using ABC 70MM sq of root length 300m | At Costing |  | Namanve
16 | KYOTERA WARID MAST | Western | RAKAI | Tx Upgrade from 100KVA to 200KVA/33KV is required, system improvement and insertion of new circuits 300M ABC 70mm2 , | At Scoping |  | SANJE
17 | OPPORTUNITY TX | Western | Rugaaga 33kv-Kyabirukwa-Kikagati 33kv | Upgrade to 200kVA/33KV, Re-inforce I phase LVACSR50 to 3phase ABC 70sqmm R/L=500m | At Scoping |  | Rugaaga
18 | KABUBU SEMA ESTATE | Central | NAKWERO 11 | injection of 100kVA, RL-HV(1000mts) and RL Lv (700mts) | Document Review |  | GAYAZA MAGIGYE
19 | Miwula Lwabenge village | Western | MITALA MARIA | Upgrade from 50KVA/33KV to 100KVA/33KV | At Scoping |  | Masaka
20 | NAKAWUKA TC NO.1 | Central | SISSA 11 Kv | Injection of 100kVA, MV (100m) and reconfigure the LV RL500 meters | At Scoping |  | ENTEBBE
21 | Kanaaba mutagubya | Central | kigo | Upgrade to 200kVA Tx, re-inforce 600m of 1phase LVACSR50 to 3phase LVACSR50 | At Drawing |  | Najjanankumbi
22 | BULEMEEZI FARM | Central | SEETA 11KV | Inject 1*100KVA 11KV/LV , Construct O/H MVACSR50 R/L=500m, re-inforce 3phase LV ABC 35SQMM X500MTRS | At Drawing |  | Namanve
23 | SSAYI ZION ESTATE | Central | KAPEKA 33KV | Inject 50kva MV rl 800mtrs and LV of 600 mtrs ABC | At Scoping |  | GAYAZA MAGIGYE
24 | KISARA VILLAGE | Central | Lugazi Town | Inject 50Kva/11kv, MV=200, LV=300 | At Drawing |  | LUGAZI
25 | Jomayi Tx | Central | NAKWERO 11kV | Inject 50Kva/11kv, MV=200, LV=300 | At Drawing |  | Namugongo
26 | MUKONO POST OFFICE | Central | KATOSI 11KV | Inject 200Kva/33kv at Kayunga Road, Construct O/H MVACSR50 R/L=100m, re-inforce 3phase Run ABC 70SQMM FOR R/L 200M | At Drawing |  | Mukono
27 | Kyazanga TC | Western | Masaka west | Upgrade existing 200KVA/33KV to 315KVA/33KV, construct 500M O/H HV, MV ACSR50 R/L=300m re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L 400m | At Scoping |  | Lyantonde
28 | Kabundi TC | Western | lyantonde Central | Upgrade from 100kVA/33kV to 200kv/33kv reinforce 1phase R/L 250 to 3phase ABC 35sqmm R/L 600 community circuit | At Scoping |  | Masaka
29 | LUBUGUMU VILLAGE | Central | KATOSI 11KV | Inject 100Kva/11kv at Lubugumu village, Construct O/H MVACSR50 R/L=300m, re-inforce 3phase Run ABC 70SQMM FOR R/L 300M | At Drawing |  | Mukono
30 | JOMAYI ESTATE BWERENGA | Central | KISUBI MISSION | Costruction of 350 Mv RL, inject 100kVA transformer together with creation of 2-500 RL LV circuits | At Scoping |  | ENTEBBE
31 | BWEYOGERERE BUTTO | Central | SEETA 11KV | Upgrade 100kVA to 200kVA and re inforcethe existing 1 phase circuit with a 3 phase circuit using ABC 70MM sq of root length 200m | At Drawing | GIS has 315kVA as existing. To contact the area team for clarification | Namanve
32 | Mbuya Police Post | Central | Mbuya 11KV | Inject 315kVA 11kV TX, Construct O/H MVACSR50 R/L=200m. re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=500m | At Scoping |  | Kitintale
33 | KASENGE VILLAGE | Central | MBALALA TC | Inject 100Kva/33kv in Kasenge tc, Construct O/H MVACSR50 R/L=300m, re-inforce 3phase Run ABC 70SQMM FOR R/L 270M | At Drawing |  | Mukono
34 | Akagetti Tx | Western | Lyantonde West | Upgrade existing 100KVA/33KV to 200KVA/33KV and re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=600m | At Scoping |  | Lyantonde
35 | Namere Village(Near Subi Health center | Central | MPERERWE 11kV | Inject 1*100Kva/11kv in NAMERE, MV=200, LV=300 | Document Review |  | Namugongo
36 | Maya Dombolo | Central | Masaka Central | Inject 50kvA/33kV/3PH,,500m ACSR 50mm2 Mv extension, 600m**2 ACSR 50MM2 of lv Single phase to 3 phase upgrade | At Drawing |  | MPIGI
37 | KAPEKE VILLAGE | Central | MBALALA TC | Inject 1*50Kva/33kv in Kapeke village, Construct O/H MVACSR50 R/L=300m, re-inforce 3phase Run ABC 70SQMM FOR R/L 270M | At Drawing |  | Mukono
38 | Total Welcome Masaka | Western | MITALA MARIA | Injection of 100KVA/33KV, Extend MV line R/L 100m and reinforcement of the LV network R/L 600m with ABC 70sqmm. | At Scoping |  | Masaka
39 | ST. MARY'S MALONGWE | Central | Lugazi Town | An Injection of 100Kva/11kv, MV=200, LV=300 | At Drawing |  | LUGAZI
40 | MUTUKULA LWAZI | Western | RAKAI | A new insertion of a 100KVA/33KV tx at Kilimiro is required 500M O/H MV ACSR 50mm2, reinfocement of Lv network radius 600M with ABC 70sqmm | At Scoping |  | SANJE
41 | Lungala Village | Central | Masaka Central 33kV | Inject 50kVA, MV line of 200m, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 300m | At Drawing |  | Natete
42 | Nsujuwe Village | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MV ACSR50 800m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=500m | At Drawing |  | Natete
43 | NAMAYINA TC | Central | NAKWERO 11 | injection of 100kVA, RL-HV(1000mts) and RL Lv (800mts) | At Scoping |  | GAYAZA MAGIGYE
44 | Bajja Tc | Western | MITALA MARIA | Upgrade to 200kv/33kv, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=300m | At Scoping |  | Masaka
45 | St. Joseph Vocational Sch, Kulambiro 100Kva | Central | kisasi 11kV | Upgrade 200kVA 11kV TX to 315kVA/11kV | At Scoping |  | Ntinda
46 | NAMUYENJE VILLAGE | Central | MBALALA INDUSTRIAL | Inject 100Kva/33kv after Namuyenje tc, Construct O/H MVACSR50 R/L=250m, re-inforce 3phase RUN 70SQMM FOR R/L 240M | At Drawing |  | Mukono
47 | Kitintale Mosque | Central | Bugolobi 11KV | Inject 200kVA 11kV TX, Construct O/H MVACSR50 R/L=300m. re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=500m | At Drawing |  | Kitintale
48 | Mwana | Central | Kireka 11KV | Inject 1x315kVA 11kV Tx ,Construct O/H MVACSR50 R/L=300m, re-inforce 1phase LV ACSR50 to 3phase Using ABC 70MMsq R/L=500m | At Drawing |  | Kitintale
49 | Kira Kiyinda No.2 | Central | Kira 11kV | Inject 200kVA 11kV TX,in kiyinda, MV=200, LV=300 | At Drawing |  | Namugongo
50 | Kirinya Kitoo Lost city | Central | Portbell | Inject 1*200kva/11kv at Kitoo lost City near Swamp, Construct O/H MVACSR50 R/L=500m, re-inforce 3phaseABC 70sqm conductor 600m | At Drawing |  | Kireka
51 | BULWANYI TC | Central | SISSA 11 Kv | Inject 100kVA, extend MV line by 500m and lV reconfiguration of 500RL 50sqmm | At Scoping |  | ENTEBBE
52 | Word of life No.3 Lumuli | Central | Kisubi 33KV | Iupgrade to 200Kva tx, re-inforce 500m of 1phase LVACSR50 to 3phase | At Drawing |  | Najjanankumbi
53 | Kachika T/C | Western | LYANTONDE CENTRAL-SEMBABULE-LWEMIYAGA 33KV | upgrade to 100kVA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=250m | At Scoping |  | Lwemiyaga
54 | Lubiigi Round About | Central | Nansana | Upgrade to 500kva | At Scoping |  | Nakulabye
55 | Lwemiyaga T/C | Western | NKONGE -KASHOZI 33KV FROM NKONGE | Upgrade from 100KVA/33KV to 200kVA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=500m | At Scoping |  | Lwemiyaga
56 | Kitintale Police Post | Central | Bugolobi 11 kV | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=300m.re-inforce 1phase LVACSR50 to 3phase 70MMsq = 300m | At Scoping |  | Kitintale
57 | NAKAGERE VILLAGE | Central | BUKERERE 11KV | Inject 100Kva/11kv at Nakagere Kyambogo Estate , Construct O/H MVACSR50 R/L=300m, re-inforce 3phase Run ABC 70SQMM FOR R/L 300M | At Drawing |  | Namanve
58 | Mutungo Tank Hill | Central | Kireka 11 kV | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=400m.re-inforce 1phase LVACSR50 to 3phase using ABC 70mm sq R/L= 450m | At Scoping |  | Kitintale
59 | BAJJO VILLAGE No. 2 | Central | BUKERERE 11KV | Inject 100Kva/11kv at Bajjo Estate, Construct O/H MVACSR50 R/L=600m, re-inforce 3phase Run ABC 70SQMM FOR R/L 300M | At Costing |  | Namanve
60 | BUKERERE COLLEGE (KIWANGO) | Central | BUKERERE 11KV | Inject 100Kva/11kv at around St. Catherine, Construct O/H MVACSR50 R/L=100m, re-inforce 3phase Run ABC 70SQMM FOR R/L 210M | At Drawing |  | Namanve
61 | NABUSUGWE JOMAYI ESTATE | Central | BUKERERE 11KV | Inject 100Kva/11kv at Nabusugwe Teso Drive, Construct O/H MVACSR50 R/L=50m, re-inforce 3phase Run ABC 70SQMM FOR R/L 150M | At Drawing |  | Namanve
62 | ST CYPRIAN KYABAKADE | Central | Ntenjeru 11kv | Inject 1*100Kva 11kv/Lv in Kyabakade tc, Construct O/H MVACSR50 R/L=200m, re-inforce 3phase Run ABC 35SQMM FOR R/L 150MTYRS | At Scoping |  | Mukono
63 | Yona Mondo | Central | Gayaza KLN 11kV | Inject 1*100Kva/11kv in Ttula , Construct O/H MVACSR50 R/L=200m, re-inforce 3phase LV ABC 35SQMM X250MTRS | At Drawing |  | Wandegeya
64 | Masozi 2 | Central | Portbell | Inject 1*200Kva/11kv in the Masozi Trading center, Construct O/H MVACSR50 R/L=400m, re-inforce 3phase LV ABC 70mm2 400m | At Drawing |  | Kireka
65 | Nkokonjeru B Musoke. | Central | Budo 11kV | Inject 50kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=550m | At Scoping |  | MPIGI
66 | JOGGO TC | Central | BUKERERE 11KV | Upgrade 100kVA to 200kVA and re inforcethe existing 1 phase circuit with a 3 phase circuit using ABC 70MM sq of root length about 150m | At Drawing |  | Namanve
67 | Twins Bar Mutungo N0.1 | Central | Kireka 11 kV | Inject 1x200kVA 11kV Tx ,Construct O/H MVACSR50 R/L=300m, re-inforce 1phase LV ACSR50 to 3phase Using ABC 70MMsq R/L=500m | At Drawing |  | Kitintale
68 | VICTORIA SEEDS | Central | Nakwero 11 kV from Namugongo | Inject 1x100kVA 11kV TX,Construct O/H MVACSR50 R/L=400m.re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=500m, | At Scoping |  | NAALYA
69 | Kololo Village No.1 | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MV ACSR50 800m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=500m | At Drawing |  | Natete
70 | Water sewage | Western | Lower ring | Transformer Injection of 200kva/11kv, Construct O/H MVACSR50 R/L=400M,Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=400m | At Scoping |  | Masaka
71 | KIRYAGONJA | Central | Namulonge 11kV feeder | Inject 1x100kVA 11kV Tx ,Construct O/H MVACSR50 R/L=1200m.re-inforcing LV 1-phase of R/L-800m to 3-phase | At Scoping |  | Bombo
72 | NSASA JOMAYI A | Central | Nakwero 11 kV from Namugongo | Construct O/H MVACSR50 R/L=100m,install 100kva/11kv/lv tx , upgrade a single phase to 3ph with ACSR50 R/L=800M | At Scoping |  | NAALYA
73 | Kawanda TC | Western | NKONGE -KASHOZI 33KV FROM NKONGE | Upgrade from 50KVA/33KV to 100VA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=300m | At Scoping |  | Lwemiyaga
74 | Nguru Water pump | Central | Kiziba | Inject 1x50kVA Tx, Construct O/H MV ACSR50 350m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=400m | At Scoping |  | Nakulabye
75 | Kijampiki TC | Western | lyantonde central | Upgrade the transformer from 50kVA/11KV to 100kVA/11KV, reinforcement of the LV network R/L 300m with ACSR50sqmm. | At Scoping |  | Masaka
76 | JINJA MISINDYE SONDE | Central | BUKERERE 11KV | Inject 100Kva/11kv at Jinja Misindye Estate , Construct O/H MVACSR50 R/L=300m, re-inforce 3phase Run ABC 35SQMM FOR R/L 300M | At Drawing |  | Namanve
77 | Kyabi A TC | Western | LYANTONDE CENTRAL-SEMBABULE-LWEMIYAGA 33KV | Upgrade from 50KVA/33KV to 100VA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=500m | At Scoping |  | Lwemiyaga
78 | BISHEKA T/C | Western | LYANTONDE CENTRAL-SEMBABULE-LWEMIYAGA 33KV | upgrade to 100kVA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=260m | At Scoping |  | Lwemiyaga
79 | Lwabenge | Western | Kalungu | upgrade from 100kva to 200kva at same position, lv reinforcement to 100sqmm five spans approx 300m | At Scoping |  | Masaka
80 | Kasasa Novitiate {St.John Mary Muzei} | Western | MITALA MARIA | upgrade to 100KVA/11KV, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=500m | At Scoping |  | Masaka
81 | Christian Centered Church Najeera | Central | kiwatule 11kV | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=100m. re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=250m | At Scoping |  | Ntinda
82 | Muwanga Rd (Kulambiro) | Central | kisasi 11kV | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=200m. re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=300m | At Scoping |  | Ntinda
83 | Mpumudde | Western | NKONGE -KASHOZI 33KV FROM NKONGE | Upgrade from 50KVA/33KV to 100VA/33KV , Inject existing 50kVA TX, Construct O/H MVACSR50 R/L=500M, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=300m | At Scoping |  | Lwemiyaga
84 | naguru police junior quarters | Central | britania | Inject 315kVA 11kV TX, Construct O/H MVACSR50 R/L=400m. re-inforce 1phase LVACSR50 to 3phase using conductor 50MM sq R/L=300m | At Drawing |  | lugogo north
85 | Kigaragi | Western | Masaka west | Upgrade the transformer from 50kVA to 100kVA only is needed | At Scoping |  | Lyantonde
86 | kyanja jomayi community police | Central | kyanja | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=200m. re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=500m | At Scoping |  | ntinda
87 | NSASA JOMAYI B | Central | Nakwero 11 kV from Namugongo | Construct O/H MVACSR50 R/L=500m,Inject 1x100kVA,re-inforce 1phase with ACSR50 R/L=600m | At Scoping |  | NAALYA
88 | JOGGO NO. 2 | Central | BUKERERE 11KV | Inject 100Kva/11kv at Joggo Kiwala trading centre, Construct O/H MVACSR50 R/L=600m, re-inforce 3phase Run ABC 70SQMM FOR R/L 250M | At Drawing |  | Namanve
89 | TAKAJUNGE BUNTUBULAMU | Central | MUKONO 2 33KV | Inject on nearby line Mpoma 11kv 200Kva 11kv/Lv in Takajunge buntubulamu, Construct O/H MVACSR50 R/L=200m, re-inforce 3phase Run ABC 70SQMM FOR R/L 150MTYRS | At Drawing |  | Mukono
90 | Racaobao Lyantonde Tx | Western | lyantonde central | Injection of 50KVA/33KV, Construct 500M O/H HV, MV ACSR50 R/L=400m re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=700m | At Scoping |  | Lyantonde
91 | Muto Complex Tx | Western | LOWERRING | Injection of 315kva/11kv,Construct U/G network R/L=200m with MV cable XLPE 95sqmm , Reinforce I phase LVACSR50 to 3phase ABC 70SQMM R/L=300m | At Scoping |  | Masaka
92 | Misindye no.1 | Central | Kyaliwajara 11 kV from Kawanda | Inject 100kVA TX, line Construct O/H MVACSR50 R/L=200m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=400m | At Scoping |  | NAALYA
93 | NABAGEREKA ECO RESORT | Central | KITALA | Upgrade to 100kVA transformer, inject existing 50kVA, extend MV line by 500m and construct 500m RL of lv network 50sqmm | At Drawing |  | ENTEBBE
94 | MITALA MARIA TC | Western | MITALA MARIA | Transformer Injection of 200kva/33kv, Construct O/H MVACSR50 R/L=100M,Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=800m | At Scoping |  | Masaka
95 | Mulawa Kawuku | Central | Kira 11kV | Inject 200Kva/11kv, MV=200, LV=300 | At Drawing |  | Namugongo
96 | VICTORY CHILD CARE | Central | Nakwero 11 kV from Namugongo | Construct O/H MVACSR50 R/L=300m,install 100kva/11kv/lv tx, upgrade a single phase to 3ph with ACSR50 R/L=400M | At Scoping |  | NAALYA
97 | Kagaba Village No.2 | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
98 | Kidda Islamic | Western | LOWERRING | Transformer Injection of 100kva/11kv, Construct O/H MVACSR50 R/L=900M,Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=650m | At Scoping |  | Masaka
99 | Kisiimu No.1 | Central | Namulonge | Inject a 100KVA, MV RL 600m ,ABC 35sqmm conductors RL700m. | At Scoping |  | Wandegeya
100 | Kizinda Village | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
101 | Masanyalaze | Central | Kololo KLN 11kV | Inject 1*200Kva/11kv in Mawanda rd , Construct O/H MVACSR50 R/L=250m, re-inforce 3phase LV ABC 35SQMM X400MTRS | At Drawing |  | Wandegeya
102 | Mukudde zone (Nyendo) tx | Western | Kalungu | Upgrade to 200KVA/11KV, Construct O/H MVACSR50 R/L=200M and inject existing transformer and reinforce 1phase to 3phase with ABC 70sqmm R/L 200m | At Scoping |  | Masaka
103 | Luvumbula Primary School | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MV ACSR50 350m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=450m | At Drawing |  | Natete
104 | MUKONO TAXI PARK | Central | MBALALA INDUSTRIAL | Inject 315Kva/11kv at Kame valley Market, Construct O/H MVACSR50 R/L=100m, re-inforce 3phase Run ABC 70SQMM FOR R/L 210M | At Drawing |  | Mukono
105 | Mabombwe Church of Uganda | Central | Wakiso | Upgrade to 100kVA, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 400m | At Scoping |  | Nakulabye
106 | Kigo village No.3 | Western | Kalungu | Upgrade from 50KVA/11KV to 100KVA/11KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=300m | At Scoping |  | Masaka
107 | Kabumbi 1 | Central | Nansana | Upgrade to 315kVA, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 350m | At Scoping |  | Nakulabye
108 | Water Pump Projects Katende | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MV ACSR50 350m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=400m | At Scoping |  | Natete
109 | KABONERA | Western | RAKAI | Tx Upgrade from 100KVA to 200KVA/33KV and reinforcement of the LV network R/L 300m with ABC 70sqmm. | At Scoping |  | SANJE
110 | Maama Kabode | Central | Kireka 11 kV | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=300m.re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=400m | At Drawing |  | Kitintale
111 | Katende Wamatovu | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
112 | Biina Kcca Qtrs | Central | Butabika 11 kV | Inject 100kVA 11kV Tx ,Construct O/H MVACSR50 R/L=300m, re-inforce 1phase LV ACSR50 to 3phase Using ABC 70MMsq R/L=500m | At Drawing |  | Kitintale
113 | Kirombe Medical Center | Central | Breweries 11 kV | upgrade 200kVA 11kV TX to 315kVA,re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L= 500m | At Drawing |  | Kitintale
114 | National Housing | Central | Masanafu | Upgrade to 315kVA, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 350m | At Scoping |  | Nakulabye
115 | KASALI | Western | KYOTERA | A new insertion of 50KVA/11KV at kasali health centre 3 Construct 500M O/H HV, MV ACSR50 R/L=200m re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=600m | At Scoping |  | SANJE
116 | Ambasda Kalongomiti | Central | Wabigalo 33kV Feeder | Inject 50kVA 33kV Tx ,Construct O/H MVACSR50 R/L=700m,construct 3phase LVACSR50 R/L=1800mtr | At Scoping |  | Luwero/wabigalo
117 | Mutebi Kabumbi | Central | Nansana | Upgrade to 315kVA, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 350m | At Scoping |  | Nakulabye
118 | Terracy garden | Central | Kireka 11 kV | Upgrade 100KvA to 200KvA and re inforcethe existing circuit with ABC 70MM sq of root length 600m | At Scoping |  | Kitintale
119 | KATUTU TX | Western | LYANTONDE CENTRAL-SEMBABULE-LWEMIYAGA 33KV | upgrade to 100kVA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=200m | At Scoping |  | Lwemiyaga
120 | Lutunku Techinical | Western | LYANTONDE CENTRAL-SEMBABULE-LWEMIYAGA 33KV | upgrade to 100kVA/33KV, Re-inforce I phase LVACSR50 to 3phase LVACSR50 R/L=300m | At Scoping |  | Lwemiyaga
121 | City Country Estates | Central | Gayaza KLN 11kV | Inject 1*100Kva/11kv in Mugalu , Construct O/H MVACSR50 R/L=200m, re-inforce 3phase LV ABC 35SQMM X200MTRS | At Scoping |  | Wandegeya
122 | Biina Tc | Central | Kireka 11 kV | Inject 1x200kVA 11kV TX, Construct O/H MVACSR50 R/L=200m. re-inforce 1phase LVACSR50 to 3phase using ABC 70MM sq R/L=400m | At Scoping |  | Kitintale
123 | Nabukalu | Central | Wakiso | Inject 1x50kVA Tx, Construct O/H MV ACSR50 650m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=450m | At Scoping |  | Nakulabye
124 | Sekiwunga T.C. | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
125 | KATUBWE VILLAGE | Central | Wakiso | Inject 1x50kVA Tx, Construct O/H MV ACSR50 800m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=500m | At Scoping |  | Nakulabye
126 | Mugema Rd; [Kawala No 05]. | Central | Nakulabye at Kla N | Upgrade to 315kVA | At Scoping |  | Nakulabye
127 | Bukuma T/C | Central | Wabigalo 33KV | Upgrade from 100kVA to 200kVA. 1 additional circuit 8 spans. | At Scoping |  | Luwero-Kasana
128 | KIBAALE | Western | RAKAI | Tx Upgrade from 200KVA to 315KVA/33KV and reinforcement of the LV network R/L 300m with ACSR50sqmm. | At Scoping |  | SANJE
129 | Mutundwe Police | Central | Bunamwaya 11kV | Install 1x100kVA with MV line of 100m, Install ABC35sqm R/L-290m, Upgrade LV 1-phase 100sqmm to ABC70sqmm R/L-115m, Reinforce 1-phase-50sqmm to 3phase 100sqmm R/L-96m, Upgrade 2-phase 100sqmm to 3-phase100sqmm R/L-50m | At Drawing |  | Nateete
130 | Rochdale Greenland sch | Central | Kakiri | Inject 1x100kVA Tx, Construct O/H MV ACSR50 350m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=400m | At Scoping |  | Nakulabye
131 | Tel Oil ,Opp Kobil | Central | Nakulabye at Kla N | Inject 315kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Scoping |  | Nakulabye
132 | Kigobe Village Booster | Central | Masanafu | Upgrade to 100kVA, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 300m | At Scoping |  | Nakulabye
133 | KASIISO RD | Central | Wabigalo 33KV | Inject 100kva MV rl 1000mtrs and LV of 800 mtrs ABC | At Scoping |  | Luwero-Kasana
134 | Katende Buye | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MV ACSR50 800m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=500m | At Drawing |  | Natete
135 | Kitende Kitovu Village | Central | Kisubi 33KV | New Tx structure, inject 100 kVA together in 4 HV spans, reinforcement of 500 | At Drawing |  | Najjanankumbi
136 | ISLAMIC PR.SCH SISSA HILL | Central | SISSA 11 Kv | Costruction of Mv 350 meters RL and lV 300 meters RL inject 100kVA 50sqmm | At Scoping |  | ENTEBBE
137 | JOVENS MAWUGULU | Central | KISUBI MISSION | Upgrading to 100kVA, inect 25kVA, construct MV of 400 LV reinforcement of 500 | At Drawing |  | ENTEBBE
138 | Kawuku | Central | Kansanga | Injection of 100kVA, MV (100m) and reconfigure the LV RL500 meters | At Drawing |  | Kabalagala
139 | Everlight | Central | Kansanga | Tx structure under line, injection of 50KVA, LV cct reconfiguration of 400m | At Drawing |  | Kabalagala
140 | Queens Ann Clinic | Central | Muyenga | Inject 50kVA Tx, MV (200m) re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=400m | At Scoping |  | Kabalagala
141 | Kitalanga Jehovah Church | Central | Kansanga | Construction of atransformer structure below the Mv line, Injection of 100kVA and reconfigure the LV RL500 meters | At Drawing |  | Kabalagala
142 | Kigoogwa 1 | Central | Bombo Industrial | Inject 50kVA 33kV Tx ,Construct O/H MVACSR50 R/L=800m,construct 3phase LVACSR50 R/L=1500mtr | At Scoping |  | Bombo
143 | Bombo Coffee Factory | Central | Namulonge Army Base | Inject 1*100KVA 11kv Transformer.Construct Mv of 100mtrs and 2 Circuits of Lv of 3 phase ABC 3 Spans ofn both sides | At Scoping |  | Bombo
144 | KAWUKU MARKET | Central | SISSA 11 Kv | Inject 50kVA, costruction of 350 Mv root lenght and 500 meters of LV towards the load centre | At Drawing |  | ENTEBBE
145 | Kitalanga Heritage | Central | Kansanga | upgrade to 315kVA Tx, re-inforce 1phase LVACSR50 to 3phase | At Drawing |  | Kabalagala
146 | BUZZI VILLAGE | Central | SISSA 11 Kv | Inject 100kVA TX below the existing line,and 500 meters RL lv circuits | At Drawing |  | ENTEBBE
147 | Bweeya Kanyigo | Central | lubowa | Inject 100kVA TX below the existing line,and 300 meters RL lv circuits | At Drawing |  | Najjanankumbi
148 | Kikubamutwe Mabike | Central | Namuwongo | Inject 50kVA Tx, MV (300m) re-inforce 400m of 1phase LVACSR50 to 3phase | At Drawing |  | Kabalagala
149 | Sweets Africa Merica | Central | Namulonge KWD 11kV | Inject 100Kva/11kv in NaKYESANJA, Construct O/H MVACSR50 R/L=700m, re-inforce 3phase LV ABC 35SQMM X300MTRS | At Scoping |  | Wandegeya
150 | Namagoma TC | Central | Masaka Central | Inject 100kVA/33kV/3Ph, 300m ACSR 50mm2 of mv extension, 600m*2 ACSR 50mm2 of lv single phase to 3 phase upgrade. | At Scoping |  | MPIGI
151 | BUPAYI VILLAGE | Central | NAMULONGE ARMY BASE | Upgrade from 25kVA to 50kVA. Replace single phase with 3 phase, Install 1 additional 3 phase circuit 3 spans. | At Scoping |  | Bombo
152 | Bugema Vocational | Central | NAMULONGE ARMY BASE | Inject 1x100kVA 11kV Tx ,Construct O/H MVACSR50 R/L=700m,construct 3phase ABC 35MM sq R/L=800mtr | At Scoping |  | Bombo
153 | WAMALA | Central | SISSA 11 Kv | Construction of atransformer structure below the Mv line towards the load centre and inject 50kVA and improve LV network 500RL | At Drawing | Approved under supplementary application 5 | ENTEBBE
154 | Nak clays | Central | Masaka Central | Inject 100KVA/33KV/3PHASE, MV length 400m*3 ACSR 50mm2, 800m*2 ACSR 50mm2 lv single phase upgrade to 3 phase. | At Drawing |  | MPIGI
155 | BUSUKUMA VILLAGE 1 | Central | UGACHICK 11 | Inject 100kVA Tx, Construct O/H line MVACSR50 R/L=0.4km , new 3phase LVACSR50 R/L=500m | At Scoping |  | GAYAZA MAGIGYE
156 | Kiwenda Nazareth | Central | NAMULONGE ARMY BASE | Upgrade existing to 50/11 and injection of existing 25KV/11Kv , Construct O/H MVACSR50 R/L-600 construct 3phase LVACSR50 R/L=600m.Reneforce existing Lv to 3 phase ABC 35mmsq RL 600 | At Scoping |  | Bombo
157 | SSINDE PAMPA ZN | Central | KISUBI MISSION | Tx structure under line, injection of 100KVA, LV cct reconfiguration with 300m | At Scoping |  | ENTEBBE
158 | Kitende Sisa Road | Central | Kisubi 33KV | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=450m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=650m | At Drawing |  | Najjanankumbi
159 | Kisozi tc | Central | Masaka Central | 2*50kVA/11KV/3phase , , MV length 1.5km*3 ACSR 50mm2, 600mACSR 50MM2 lv single phase to 3phase upgrade | At Scoping |  | MPIGI
160 | BUKANDEKANDE VILLAGE | Central | KISUBI MISSION | Costruction of 350 Meters RL MV Inject 50kVA and 500 meters RL lv circuits using 50sqmm | At Drawing |  | ENTEBBE
161 | Gangu Central | Central | kigo | Inject 50kva tx, MV (200m), re-inforce 300m of 1phase LVACSR50 to 3phase | At Drawing |  | Najjanankumbi
162 | Lesparacy Mirembe | Central | kigo | Inject 50kVA Tx, MV (300m) re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=550m | At Drawing |  | Najjanankumbi
163 | Gombe Kitasa TC | Central | Kakiri | Upgrade to 200kVA, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 350m | At Scoping |  | Nakulabye
164 | Wakimese No.1 | Central | Budo 11kV | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=400m | At Scoping |  | MPIGI
165 | Wakimese No.3 | Central | Budo 11kV | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=650m | At Scoping |  | MPIGI
166 | Katende Mission | Central | Masaka Central 33kV | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
167 | NALUGALA KABONA | Central | KISUBI MISSION | Maintain the existing 200 kVa & inject 100kVA then centre with load Costruction of transfomer struture below and split lv circuits Rl 500 meters 50sqmm | At Scoping |  | ENTEBBE
168 | KIGUNGU TC | Central | KITOORO | Inject 50kVA TX with a new transfomer struture below the existing line in the load centre and split lv circuits by construction of 500 RL lv network | At Drawing |  | ENTEBBE
169 | Kavule TC. | Central | Masaka Central 33kV | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
170 | Kitemu kivu | Central | Masaka Central | Inject 50kVA/33KV/3PH.,MV length 400m*3ACSR 50mm2, 600m*2 ACSR50mm2 of lv single phase upgrade network | At Scoping |  | MPIGI
171 | Nakitokolo village | Central | Masaka Central | Inject 100KVA/33KV/3PH, 400m*3 of MV extension,800m*2 ACSR 50mm2 of lv single phase to 3 phase upgrade | At Scoping |  | MPIGI
172 | Kyambazzi Kyampisi | Central | Masaka Central | Inject 50kVA/33KV/3phase, 700m*3 ACSR 50mm2 mVextension, 1.2km*2 of lv single phase to 3 phase upgrade | At Scoping |  | MPIGI
173 | Kireka Bombastic Club | Central | Mityana | Inject 50kvA/33kV/3PH,,500m ACSR 50mm2 Mv extension, 600m**2 ACSR 50MM2 of lv Single phase to 3 phase upgrade | At Scoping |  | Natete
174 | MASOLI | Central | UGACHICK 11 | Inject 100kVA Tx, Construct O/H line MVACSR50 R/L=1.2km , new 3phase LVACSR50 R/L=500m Renforce 1phase to 3phase of RL 800m | At Scoping |  | GAYAZA MAGIGYE
175 | Mabanga village | Central | Masaka Central 33kV | Inject 100kVA Tx, Construct O/H MV ACSR50 650m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=450m | At Drawing |  | Natete
176 | Kyengera Masanda Zone. | Central | Budo 11kV | Inject 1x100kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Scoping |  | MPIGI
177 | Kyeyitabya Village | Central | Masaka Central 33kV | Inject 1x50kVA Tx, Construct O/H MVACSR50 R/L=100m, re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=350m | At Drawing |  | Natete
178 | Kiwoko rd miller | Central | Luwero Town 11kV Feeder | Inject 50kVA 11kV TX, Construct O/H MVACSR50 R/L=600m, construct 3phase LVACSR50 R/L=1200m | At Scoping |  | Luwero/wabigalo
179 | KAKINDU VILLAGE | Central | KAWUKU | Costruct 600 meters RL Mv network Injection 100kVA, create Lv new circuits RL 600meters with 50sqmm | At Drawing |  | ENTEBBE
180 | Mpambire TC | Central | Masaka Central | Inject 50kVA/33kV/3PH, 100m*3 ACSR 50mm2 of MV extension, 800m*2 ACSR 50mm2 of lv single phase to 3 phase upgrade. | At Scoping |  | MPIGI
181 | Musana Zone. | Central | Mityana | Inject 50kVA/33kV/3PH, 100m*3 ACSR 50mm2 of MV extension, 800m*2 ACSR 50mm2 of lv single phase to 3 phase upgrade. | At Drawing |  | Natete
182 | Gogonya Village No.2 | Central | Mityana | Inject 200kVA/33kV/3PH, 100m*3 ACSR 50mm2 of MV extension, 800m*2 ACSR 50mm2 of lv single phase to 3 phase upgrade. | At Drawing |  | Natete
183 | Gogonya Village No.3 | Central | Mityana | Inject 200kVA/33kV/3PH, 100m*3 ACSR 50mm2 of MV extension, 800m*2 ACSR 50mm2 of lv single phase to 3 phase upgrade. | At Scoping |  | Natete
184 | mabuye no 1 | Central |  | Inject 1x50kVA Tx, Construct O/H MV ACSR50 450m, re-inforce 1phase LV ACSR50 to 3phase LV ACSR50 R/L=600m | At Scoping |  | Natete
185 | Nkokonjeru No.2 | Central | Budo 11kV | Re-inforce 1phase LVACSR50 to 3phase LVACSR50 R/L=450m | At Scoping |  | MPIGI
186 | sumaya Nsangi | Central | Masaka Central | 50kVA/33kV/3PH,900m ACSR 50mm2 of mv extension, reforce 600m ACSR 50mm2 of lv single phase to 3 phase upgrade | At Scoping |  | MPIGI
187 | BUKWO MARKET | Eastern | BUKWO 33KV FROM KERE | Upgrade to 100kva, Construction Lv 3 Phase route lrngth 500m | At Scoping |  | Bukwo
188 | Lolachat Health center 3 | Eastern | Nakapiripirit33kv@Mororo | Upgrade to 100kVA, Inject existing 50kVA to supply quality power to lolachat S.School and Updf barracks and the sorraunding community, MV=250m and LV=350m | At Scoping |  | Nakapiripirit
189 | Relax lodge | Eastern | Nakapiripirit 33kv@Moroto | Upgrade to 100kVA, and inject existing 50kVA to improve the voltage profile, MV=200m, LV=400m | At Scoping |  | Nakapiripirit
190 | Namalu Tc | Eastern | Nakapiripirit 33kv@Moroto | Upgrade to 100kvA, uprade 500m of single phase line to three phase. Inject existing 50kVA next to st.mary's day and boarding primary school with MV line of 300m | At Scoping |  | Nakapiripirit
191 | Nakapiripirit Tc | Eastern | Nakapiripirit 33kv@Moroto | Upgrade to 100kVA, inject existing 50kVA in areas of Nangromit near health centre 3. Extend MV of 200m Upgrade the existing single phase to three phase line with 700m | At Scoping |  | Nakapiripirit
192 | Amudat Hospital | Eastern | Nakapiripirit 33kv@Moroto | Upgraded to 100kVA and relocate it to the centre of the load. Upgrade 400m of single phase to three phase, MV=200m | At Scoping |  | Nakapiripirit
193 | Benyinyi | Eastern | BUKWO 33KV FROM KERE | Injection 100Kva tx, Construction mv line route length 60m, Lv 3 phase 500m | At Scoping |  | Bukwo
194 | Ttamu Hill | Northern | Mutundwe | Inject 100kva/ 33kv/415v by constructing an MV line of about 7 poles and 4 spans of lv one cct . | At Scoping |  | Mityana
195 | Kyengeza Parish S.S.S | Northern | Mutundwe | Inject 100kva /33kv/415v by constructing an MV line of about 8 poles and 4 spans of 3 phase lv cct . | At Scoping |  | Mityana
196 | Kibibi Water Pump | Northern | Kibibi | Inject 100kva /11kv/415v by constructing an MV line of about 6 poles and 3 spans of lv network one cct | At Scoping |  | Mityana
197 | Lubanja Village No.1 | Northern | Namutamba | Inject 100kva/ 11kv/415v by constructing an MV line of about 8 poles and 4 spans lv cct | At Scoping |  | Mityana
198 | Kitongore | Western | Ibanda 33kV - Kazo T-Off | Upgrade existing to 200 kVA, inject 50kVA with 200m of MV extension and LV of 300m | At Scoping |  | KAZO
199 | Mgm Barracks staff Qtrs | Eastern | Magamaga town | Inject 200kva /11k, extend MV by 200m and re-inforce lv line by 300m | At Scoping |  | Jinja
200 | bukwo elite | Eastern | BUKWO 33KV FROM KERE | Upgrade to 100kva, Inject existing 50kVA, MV line 500m, Construction Lv 3 Phase route lrngth 500m | At Scoping |  | Bukwo
201 | Masindi main market atc | Northern | Masindi township | Upgrade to 100kva/11kv/LV, reinforce 300m of LV | At Scoping |  | Masindi
202 | Butaswa Kaqungwa | Eastern | Kasolwe | Upgrade the Transformer to 200kVA and inject existing 100kVA, MV=200 | At Scoping |  | Kamuli
203 | Apokor Merikit Road | Eastern | Tororo 1 | Injection 100Kva, construction of MV line 100M route lengt, Lv 3 Phase 500m | At Scoping |  | Tororo
204 | Busolwe 2 Round about | Eastern | Butalejja | injection 50Kva ,construction mv line route length 200m Lv 3 phase 500m | At Scoping |  | Tororo
205 | Mile 8 mbale road | Eastern | Tororo 1 | Upgrade to 100Kva , Construction Lv 3 Phase route lrngth 500m | At Scoping |  | Tororo
206 | Akapa TC | Eastern | Tororo Ring 1 | Injection 100Kva ,Construction mv line route length 200m, lv 3 phase 500m | At Scoping |  | Tororo
207 | Manjasi | Eastern | Town Via Quarry | Injection of 100kva, Construction of Mv line route Length 400m, Lv 3 phase 500m | At Scoping |  | Tororo
208 | Busia ss | Eastern | Busia | Inject 100 Kva tx, construct MV route length 600m,Lv 3 phase 500m | At Scoping |  | Busia
209 | Hon Wejuli | Eastern | Busia | Upgrade to 100Kva tx, Construct LV 3 Phase line route lrngth 500m | At Scoping |  | Busia
210 | kigumba petro | Northern | Kigumba | Needs an upgrade to 200kva/11kv, LV reinforcement | At Scoping |  | Masindi
211 | Butiru TC | Eastern | Tororo 1 | Injection 50Kva , Construction MV line route Length 600m, LV 3 Phase 500m | At Scoping |  | Tororo
212 | kabango tc | Northern | Budongo | Needs an upgrade to 200kva/11kv/LV and create a new circuit at the transformer structure, | At Scoping |  | Masindi
213 | Kirasa 1 | Northern | Masindi township | Needs an upgrade to 200kva/11kv | At Scoping |  | Masindi
214 | bungokho sub-county | Eastern | Mbale 1 33 kV from Tororo Main | Construct OH line of RL 900m, inject a 100kva, lv 1-ph network upgrade to 3phase 400m upgrade of 3phase 25mmsq to 3phase 50mmsq of RL 400m. | At Scoping |  | Mbale
215 | kasanvu tc | Eastern | Mbale Ring 1 11 kV from Mbale | Inject 50kva, construct hv overhead line 500m and upgrade existing lv network to 3ph 400mtr | At Scoping |  | Mbale
216 | Mukuju PTC | Eastern | Tororo 1 | Injection 100Kv,C0nstruction Mv line route Length 500m, Lv 3 phase 500m | At Scoping |  | Tororo
217 | Masindi Hotel | Northern | Nyamigisa | Injection of 200kva /11kv at the existing tx structure,extension of MV line R/L 150 mtrs,reinforcement of LV line R/L 300 mtrs and relocation of the existing 200kva/11kv at Timber factory | At Scoping |  | Masindi
218 | Kabimbiri RC | Eastern | Nakifuma 11kV | Inject 100kva, construct MV of 150m and improve 250m of LV 1-Phase to 2-3-phase | At Scoping |  | Kayunga
219 | Mayuge Health Centre IV | Eastern | JinjA INDUSTRIAL | Upgrade the Transformer to 200kVA | At Scoping |  | Mayuge
220 | Budebe Town Council | Eastern | JinjA INDUSTRIAL | Upgrade the Transformer to 200kVA | At Scoping |  | Mayuge
221 | MATANY T.C | Eastern | F. CEMENT 3 | Transformer injection1x 100KV/33Kv , MV of 200Mtr and LV of 300m | At Scoping |  | Moroto
222 | Katwe Road | Eastern | kangulumira | Inject 100kva, construct MV of 100m and improve 200m of LV 1-Phase to 2-3-phase | At Scoping |  | Kayunga
223 | Makindye Road | Eastern | kangulumira | Inject 100kva, construct MV of 100m and improve 350m of LV 1-Phase to 2-3-phase | At Scoping |  | Kayunga
224 | Nakaliro Village | Eastern | Bbaale 33kV | Inject a 200kVA Transformer, extend MV by 100m and LV by 250m | At Scoping |  | Kayunga
225 | kikwanya rd | Eastern | kangulumira | Inject 100kva and improve 300m of LV 1-Phase to 2-3-phase | At Scoping |  | kayunga
226 | NAMANYONYI T/C | Eastern | Mbale Ring 1 11 kV from Mbale | Inject a 50kva transformer, construct OH line of RL 800m, lv 1-ph network upgrade to 3phase 400m, new 3phase of RL 300m. | At Scoping |  | Mbale
227 | Kyampisi TC | Eastern | kangulumira | Inject 100kva, construct MV of 200m and improve 300m of LV 1-Phase to 2-3-phase | At Scoping |  | Kayunga
228 | WORKS | Eastern | CEMENT 1 | Transformer injection 100KV/33Kv , MV 300Mtr of 50mmsq and LV 500 | At Scoping |  | Moroto
229 | MOROTO BARRACKS UPPER | Eastern | CEMENT 1 | Transformer upgrade from 100KVA to 200KVA ,upgrade of conductors ,100mmsq ,600M and poles | At Scoping |  | Moroto
230 | maluku D.A | Eastern | Mbale Ring 2 11 kV from Mbale | Inject a 100kva, construct OH line of RL 700m, upgrade lv 1-ph network to 3ph 400mtr | At Scoping |  | Mbale
231 | Kamuli Kiyunga | Eastern | Kamuli 33kV | Upgrade TX to 315kVA/33kV | At Scoping |  | Kamuli
232 | nabumali tc | Eastern | Bugema 11 kV from Mbale | Inject a 50kva, construct OH line of RL 1100m, New 3phase of RL 300m, upgrade lv 1phase ACSR25mmsq to 3phase ACSr50mmsq of RL 300m. | At Scoping |  | Mbale
233 | Namayumba Town | Northern | Kiziba 11kv | Inject a 100kva/33kv/415v by constructing an MV line of about 6 MV poles and about 8 spans of 3 phase lv network on two lv ccts | At Scoping |  | KAPEKA
234 | KATAKWI CENTRAL POLICE TX | Eastern | OPUYO MOROTO | Injection 100Kva tx, Construction mv line route length 60m, Lv 3 phase 202m | At Scoping |  | Katakwi
235 | Kakira town council | Eastern | Iganga | Upgrade from 100kva/11kv to 200kva/11kv, construct another circuit of 300m | At Scoping |  | Jinja
236 | NAMUNSI | Eastern | Mbale Ring 1 11 kV from Mbale | Inject a 50kva, construct OH line of RL 1000m, New 3phase of RL 300m, upgrade lv 1phase ACSR25mmsq to 3phase ACSr50mmsq of RL 400m. | At Scoping |  | Mbale
237 | Butare | Western | Tea Estate 11kv from Ishaka | Inject 200kva transformer and Install MV line 1 span. 2 circuits 3 phase 4spans each. | At Scoping |  | Bushenyi
238 | Achet Tx | Northern | Bobi - Oyam | injection of 50kVA, RL-HV(200mts) and RL Lv (50mts) | At Costing |  | Gulu
239 | palisa | Eastern | palisa 11kv | inject 200kva Tx, construct mv route length 500m, construct lv 3phase route length 500m | At Scoping |  | Pallisa
240 | BAZAR | Eastern | CEMENT 1 | Transformer injection 200KV/33Kv , MV (200m) and LV (450m) | At Scoping |  | Moroto
241 | Kizinda | Western | Tea Estate 11kv from Ishaka | inject 200kva transformer and Install MV line 1 span. 2 circuits 3 phase 5 spans each. | At Scoping |  | Bushenyi
242 | REGINA MUNDI | Eastern | CEMENT 1 | Transformer injection 200KV/33Kv , MV (300m) LV (300m) | At Scoping |  | Moroto
243 | MOROTO BARRACKS UPPER | Eastern | CEMENT 1 | Transformer UPGRADE from 200KVA to 315KVA ,upgrade of conductors ,100mmsq ,600M and poles | At Scoping |  | Moroto
244 | budaka c | Eastern | kibuku tirinyi 11kv | Inject 200kva Tx, construct MV line of 200m and lv line 3phase Route length 200m | At Scoping |  | Pallisa
245 | KASENYI | Western | Rukungiri 33 kV from Ishaka | Inject 200kva transformer and Install MV line 1 span. 2 circuits 3 phase 3 spans each. | At Scoping |  | Bushenyi
246 | Kitimbwa Police | Eastern | Bbaale 33kV | Inject a 200kVA Transformer, extend MV by 200m and LV by 300m | At Scoping |  | Kayunga
247 | Bweyale 1 | Northern | kigumba | Needs a 200kva/33kv/LV transformer injection with two new circuits. | At Scoping |  | Masindi
248 | sebei diocese | Eastern | BUKWO 33KV FROM KERE | Upgrade to 100kva, injection of existing 50kVA, MV line 500m, Construction Lv 3 Phase route length 500m | At Scoping |  | Bukwo
249 | Wakitaka TC | Eastern | Mutai | Upgrade from 100kva/11kv to 200kva/11kv and relocate 100kva/11kv TX with lv upgrade of 300m from single to 3 phase | At Scoping |  | Jinja
250 | Swam boarder | Eastern | BUKWO 33KV FROM KERE | Upgrade to 200kva, Construction Lv 3 Phase route lrngth 500m | At Scoping |  | Bukwo
251 | Mawero 2 Verdit | Eastern | Busia | Inject 100Kva Tx, construct MV of 300m and Lv line route length 500m | At Scoping |  | Busia
252 | Railway station | Eastern | Town | Upgrade from 100kva/11kv to 200kva/11kv, run another circuit with 300m | At Scoping |  | Jinja
253 | AMURIA 2 TX | Eastern | OPUYO MOROTO | Injection 100Kva tx, Construction mv line route length 60m, Lv 3 phase 201m | At Scoping |  | Katakwi
254 | Cole magamaga barracks | Eastern | Magamaga town | Inject 200kva /11kv and re-inforcement of lv line with 200m | At Scoping |  | Jinja
255 | Busana TC | Eastern | Bbaale 33kV | Upgrade the Transformer to 200kVA | At Scoping |  | Kayunga
256 | Mpumudde TC | Eastern | Mutai | Inject 200kva /11kv and re-inforcement of lv line of 400m | At Scoping |  | Jinja
257 | KASANVU | Eastern | Mbale Ring 1 11 kV from Mbale | Upgrade to 100kva, lv 1-ph network upgrade to 3phase 300m | At Scoping |  | Mbale
258 | Pajule tarding Center tx | Northern | Kitgum 33kv from Lira main/Agago | Inject 50kVA, MV line of 500m and LV line of 400m | At Scoping |  | KITGUM
259 | Oriamo Tc | Northern | OLWENY- DOKOLO | Upgrade of 25KVA 1Q to 50KVA 3Q , upgrade the conductor size from 50mm bare to 35mm ABC cable 400m, upgrade transformer structure from one pole structure to a complete plateform, 2 pole 12M, and other TX platform accessories, | At Scoping |  | Dokolo
260 | Aboke corner mollemTC | Northern | Aboke 33kv | TX upgrade from 200kVA/33kv to 315kVA/33kv | At Drawing |  | Kamdin
261 | Kanyamabona | Western | Rukungiri 33 kV from Ishaka | Inject 50kva transformer and expand Install MV line 1 span. 2 circuits 3 phase 3 spans each. | At Scoping |  | Bushenyi
262 | UEDCL YARD | Eastern | CEMENT 1 | Transformer injection 2x 100KV/33Kv , MV (800m) and LV (1000m) | At Scoping |  | Moroto
263 | Barrio TC | Northern | Aboke 33kv | Inject 50KVA, MV line 400m LV line 500m | At Scoping |  | Kamdin
264 | KYANGWALI 2 | Northern | BUSERUKA MUTEME | inject a 100kva by constructing an Mv line of about 5 poles and 8 spans of two three phase lv ccts | At Scoping |  | KABWOYA
265 | Kapchesy | Eastern | BUKWO 33KV FROM KERE | Upgrade to 100kva, inject existing 50kVA, MV line 500m, Construction Lv 3 Phase route lrngth 500m | At Scoping |  | Bukwo
266 | Nangwe Atc | Eastern | Busia | Inject 100Kva tx, Construct MV line route Length 600m, Lv 3 phase 500m | At Scoping |  | Busia
267 | Kashenshero TC | Western | Rukungiri 33 kV from Ishaka | inject 100kva transformer and Install MV line 1 span. 2 circuits 3 phase 5 spans each. | At Scoping |  | Bushenyi
268 | Misago | Northern | Busunjju | Upgrade to 200Kva/33kv | At Scoping |  | Hoima
269 | kasawo tc | Eastern | nakifuma town | Inject 100kva, extend MV by 200m and improve LV 1-Phase to 2-3-phase by 300m | At Scoping |  | kayunga
270 | Namuro | Eastern | Mbale 2 33 kV from Tororo Main | Inject 100kva, MV line of 500m and lv single phase to 3phase overhead 300m overhead | At Scoping |  | Mbale
271 | Koranolya Rwebishuri village | Western | Lyantonde West 33kV from Mmbarara central | Injection 50kva transformer, MV line of 200m and expand run 3phase for 500mtrs on both circuits | At Scoping |  | Mbarara
272 | Bugongi town | Western | Ishaka Town 11 kV from Ishaka | inject 100kva transformer and Install MV line 1 span. 2 circuits 3 phase 5 spans each. | At Scoping |  | Bushenyi
273 | Namaubi village/Olivia Petroleum | Eastern | Busia | Inject 100Kva tx, construct Mv line route Length 100m, L 3 phase 500m | At Scoping |  | Busia
274 | Bugemba Village | Eastern | JinjA INDUSTRIAL | Upgrade the transformer to 200kVA | At Scoping |  | Mayuge
275 | Kainogoga mosque | Eastern | Mutai | Upgrade from 100kva/11kv to 200kva/11kv | At Scoping |  | Jinja
276 | Wanyama upper village | Eastern | Wairaka | Upgrade from 100kva/11kv to 200kva/11kv | At Scoping |  | Jinja
277 | Namagera TC | Eastern | Kamuli 33kV | Upgrade TX to 315kVA/33kV | At Scoping |  | Kamuli
278 | Padwong tx | Northern | Ayul 11kv from Kitgum | Inject 50kva/11kv, extention of MV line R/L 600mtrs,reinforcement of the existing LV line R/L 400mtrs | At Scoping |  | KITGUM
279 | Kakukwuru 1 | Eastern | Nakifuma 11kV | Upgrade the Transfromer to 200kVA | At Scoping |  | Kayunga
280 | KAPEEKA TC | Northern | Kapeka Industrial | Inject a 100kva/33kv/415v by constructing an MV line of about 5 MV poles and about 8 spans of 3 phase lv network on two lv ccts | At Scoping |  | KAPEKA
281 | Butema SDA Church | Eastern | Lugazi 11 kV from Njeru | Injection of 50kva /11kv,extension of MV line of 200m and Relocate the Existing 25KVA Transformer | At Costing | The 25kVA transformer failed on overload and therefore the scope for relocation was discarded | Jinja
282 | Kamulikwizi No.3 | Western | Kasese 33 kV from Nkenda | Upgrade from 25kVA to 50kVA, reinforce single to 3 phase length 500m. | At Scoping |  | Kasese
283 | Kasese rd | Western | Ishaka Town 11 kV from Ishaka | inject 100kva transformer and Install MV line 1 span. 2 circuits 3 phase 5 spans each. | At Scoping |  | Bushenyi
284 | koriri rd sironko | Eastern | Mbale Ring 1 11 kV from Mbale | Inject a 100kva, construct OH line of RL 800m, upgrade lv 1phase ACSR25mmsq to 3phase ACSr50mmsq of RL 400m. | At Scoping |  | Sironko
285 | diamont trust bank | Eastern | Mbale Ring 2 11 kV from Mbale | Inject 200kVA Tx, Construct O/H line MVACSR50 R/L=1km , new 3phase LVACSR50 R/L=500m Renforce 1phase to 3phase of RL 500m | At Scoping |  | Mbale
286 | Kihumuro UPTC | Western | Kabale west 11kV | Construct Mv 300mt,Inject 100kVA,Upgrade Lv 200mt proposed location at kihumuro army barrack | At Scoping |  | Kabale
287 | Bulo Tc | Northern | Kabulasoke 11 kV from Kiriri | Inject 100kva/ 11kv/415v by constructing an MV line of about 7 MV poles and about 4 spans of two lv ccts | At Scoping |  | Mityana
288 | MUNGONYA | Western | Ntare | Inject in 100kva and upgrade network to3-PHASE.Inject the transformer near Omugabe tombs by moving the MV for 1km and run 3phase for 240mtrs on both circuits | At Scoping |  | Mbarara
289 | Wairaka village | Eastern | Wairaka | Upgrade from 50kva/11kv to 100kva/11kv and relocate the 50kva/11kv | At Costing |  | Jinja
290 | Kanoni Saza Hqters | Northern | Kabulasoke 11 kV from Kiriri | Upgrade from 50kVA to 100kVA. Extend 2 spans, 1 additional circuit. | At Scoping |  | Mityana
291 | Mabanga T.C | Western | Rukungiri 33 kV from Ishaka | Upgrade from 50kVA to 100kVA. Re-inforce 400m of LV | At Scoping |  | Rukungiri
292 | Mwitazinge | Northern | Ndibata-Kakumiro | Inject 200kVA since the town is growing at a very high speed and there are potential three phase customers , construct an MV line of about 6poles and 6 spans of lv two ccts 3 phase | At Scoping |  | Kisiita
293 | kadama M | Eastern | kibuku tirinyi 11kv | inject 100kva Tx, construct mv rout length 150m, construct lv 3phase route length 500m, 2phase 150m | At Scoping |  | Pallisa
294 | Nyamitanga Catholic Parish | Western | Karamurani | Inject 200kva Tx,construct h.v line five spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
295 | Gatsbay Tree Project | Western | Lyantonde West | Inject 100kva Tx,construct h.v line four spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
296 | Jeka Farm Limited | Eastern | Bulopa | Upgrade the Transfromer to 200kVA | At Scoping |  | Kamuli
297 | Mafubira lower | Eastern | Mutai | Upgrade from 100kva/11kv to 200kva/11kv. | At Scoping |  | Jinja
298 | Mudwaniro | Western | Rukungiri 33 kV from Ishaka | Upgrade from 50kVA to 100kVA. Re-inforce 400m of LV | At Scoping |  | Rukungiri
299 | Otwal Railway | Northern | Aboke 33kv | TX upgrade from 100kVA/33kv to 315kVA/33kv and introducing a second circuit. ABC 4core - 350mts | At Scoping |  | Kamdin
300 | Omukarera | Western | Mpanga 2 33 kV feeder from Rugonjo | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
301 | Total petrostation | Eastern | Town | Upgrade from 100kva/11kv to 200kva/11kv | At Scoping |  | Jinja
302 | Kabutsye | Western | Ishaka 11 kV from Mbarara Central | Upgrade from 50kVA to 100kVA. Install 2 circuits three phase, 5 spans each. | At Scoping |  | Bushenyi
303 | Warid tx | Northern | Layibi 11kv from Gulu | Upgrade to 200kva /11kv | Document Review |  | Gulu
304 | Kashekuro TC | Western | Ishaka Town 11 kV from Ishaka | Inject 50kva transformer and Install MV line 1 span. 2 circuits 3 phase 3 spans each. | At Scoping |  | Bushenyi
305 | Katete Kateebero Tc | Western | Kikagati | Inject 200kva Tx,construct h.v line five spans and construct two lv ccts of three spans 3phase @cct | At Scoping |  | Mbarara
306 | Dumba | Western | Bundibugyo 33 kV from Fort Portal | Inject a 200 kVA transformer, construct 2 spans of Hv, 2 ccts of 3 spans LV. | At Scoping |  | Bundibugyo
307 | Sedrac | Western | Kyenjojo 33 kV from Rugombe | Inject a 200 kVA transformer, construct 3 spans of Hv, 2 ccts of 3 spans LV. | At Scoping |  | Kyegegwa
308 | Abalodyangang | Northern | LWALA NAMASALE | Inject 50KVA, MV line 400m LV line 500m | At Scoping |  | Amolatar
309 | Kanyamatambala | Western | Ishaka Town 11 kV from Ishaka | upgrade from 25KV single phase to 50kva 3phase and reconfigure the Lv to 3phase for about 4 spans on each of the two circuits created. | At Scoping |  | Sheema-Kabwohe
310 | Ssemuto Town | Northern | Kiziba 11kv | Inject a 100kva/33kv/415v by constructing an MV line of about 07 MV poles and about 7 spans of 3 phase lv network | At Scoping |  | KAPEKA
311 | Customs Tx 1 | Western | Kikorongo-Mpondwe 33 kV from Nkenda | Inject a 200 kVA transformer, construct 2 spans of Hv, 2 ccts of 3 spans LV. | At Scoping |  | Mpondwe
312 | Rulembo tx | Western | Mubende 33 kV from Nkonge | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kyegegwa
313 | TOWN CENTRE 1 | Western | Kasese Town 11 kV from Kasese | Upgrade to 315kVA 11 kV, add protection and improve tx wiring. | At Scoping |  | Kasese
314 | Bamunanika Village | Northern | Kasanda 33 kV from Mityana | Inject 1*50kVA transformer. MV line of 200m, 2 LV circuits 7 spans each. | At Scoping |  | Mityana
315 | Merryland water Pump | Eastern | Busia | Inject 100Ka tx, Construct MV of 250m and LV 3 phase route Length 500m | At Scoping |  | Busia
316 | Nyahuka | Western | Bundibugyo 33 kV from Fort Portal | Inject a 200 kVA transformer, construct 2 spans of Hv, 2 ccts of 3 spans LV. | At Scoping |  | Bundibugyo
317 | RUHARO VILLAGE | Western | Ishaka | Injection of 100kVA transformer and Upgrade network to 3-phase.Inject the transformer around Dr. Biteks Apartments, create a t-off of 150mtrs and put 3phase for 360mtrs for two circuits | At Scoping |  | Mbarara
318 | KATANGA T.C | Eastern | CEMENT 1 | Transformer injection 100KV/33Kv , MV line of 300m, LV of 300Mtr of 50mmsq and poles | At Scoping |  | Moroto
319 | KANGOLE T.C | Eastern | F. CEMENT 3 | Transformer injection 100KV/33Kv , MV line of 300m, LV of 300Mtr of 50mmsq and poles | At Scoping |  | Moroto
320 | MOROTO MOUNT | Eastern | CEMENT 1 | Transformer injection 100KV/33Kv , MV line of 300m, LV of 300Mtr of 50mmsq and poles | At Scoping |  | Moroto
321 | Kakyeka Area | Western | Ishaka | Upgrade to 200kva 3phase Tx, Upgrade lv cdtor size from 25mmsq to 50mmsq 3phase | At Scoping |  | Mbarara
322 | Nyaruziba | Western | Kagadi 33 kV from Muzizi | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kagadi
323 | Nyakabirizi Tc | Western | Ishaka Town 11 kV from Ishaka | Inject 100kva transformer and Install MV line 1 span. 2 circuits 3 phase 4 spans each. | At Scoping |  | Bushenyi
324 | Mugarutsya | Western | Ishaka 33kV from Mbarara North | Upgrade from 100KVA to 200KVA,shift the transformer structure to closer the load centre and factory | At Scoping |  | Sheema-Kabwohe
325 | Nyarukoma 2 | Western | Kyenjojo 33 kV from Rugombe | Upgrade to 200 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kyenjojo
326 | County Agric Dpt Prgm Mafubira | Eastern | Mutai | Uprade from 200kva/11kv to 315kva/11kv, construct another circuit of 250m | At Scoping |  | Jinja
327 | kyeitembe | Western | Ishaka Town 11 kV from Ishaka | Upgrade from 50kVA to 100kVA. Install 1 additional circuit 3 phase 5 spans, improve to 3 phase the existing line 6 spans. | At Scoping |  | Bushenyi
328 | Budaka Township | Eastern | Kibuku Tirinyi | Inject 100kVA Tx, Construct O/H line MVACSR50 R/L=0.2km , new 3phase LVACSR50 R/L=500m Renforce 1phase to 3phase of RL 300m | At Scoping |  | Mbale
329 | kalaki L | Eastern | palisa 11kv | upgrade to 50kva Tx, construct mv route length 300m, construct lv 500m | At Scoping |  | Pallisa
330 | Alwa | Northern | OLWENY- DOKOLO | Upgrade of 100KVA to 200KVA to cater for all the three mills in TC | At Scoping |  | Dokolo
331 | Kabutsya 1 | Western | Ishaka 11kV from Mbarara Central | Inject a 50kva in Kabutyse town,create two circuits on the new structure and re-configure atleast 4 spans to 3phase. | At Scoping |  | Sheema-Kabwohe
332 | Harugare | Western | Bundibugyo 33 kV from Fort Portal | Inject a 50 kVA transformer, construct 3 spans of HV, 1 cct of 4 spans LV. | At Scoping |  | Bundibugyo
333 | Busy Bee-Buhura | Western | Ishaka 33 kV from Mbarara North | Upgrade from 25kVA to 50kVA. Replace single phase with 3 phase, Install 1 additional 3 phase circuit 3 spans. | At Scoping |  | Bushenyi
334 | Sesanga | Western | Kikagati | Upgrade to 50kva Tx, construct one lv ccts of five spans 3phase | At Scoping |  | Mbarara
335 | Nyabugando Tx | Western | Kikorongo-Mpondwe 33 kV from Nkenda | Insertion of 315 kVA Tx to cater for the voltage drop(185v) during peak hours. Construct 5 spans of HV and 2 ccts of 3 spans each. | At Scoping |  | Mpondwe
336 | Kyabenda Cou | Western | Mpanga 2 33 kV feeder from Rugonjo | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
337 | Busunga 2 | Western | Bundibugyo 33 kV from Fort Portal | Upgrade 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Bundibugyo
338 | Nyabitusi Maize Mill 1 | Western | Mpanga 2 33 kV feeder from Rugonjo | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
339 | Kitakule tx(Kabale diary) | Western | Kikagati | Inject 100kva Tx,construct h.v line five spans and construct two lv ccts of five spans 3phase@cct | At Scoping |  | Mbarara
340 | Katookye Village | Western | Ishaka 11 kV from Mbarara Central | Upgrade from 50kVA to 100kVA, install 1 additional 3 phase circuit, 4 spans. | At Scoping |  | Bushenyi
341 | Kasese Railway Station | Western | Kasese Town 11 kV from Kasese | Inject 1*100kVA transformer, install two 3 phase circuits, length 500m each. | At Scoping |  | Kasese
342 | Katete TC NO.3(Katete beach) | Western | Kikagati | Inject 100kva Tx,construct h.v line two spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
343 | Ganyenda 1 | Western | Mpanga 2 33 kV feeder from Rugonjo | Upgrade to 200 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
344 | Rubona | Western | Ibanda-Kabujjogera | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
345 | Katobu Tx | Western | Rukungiri 33 kV from Ishaka | Upgrade from 200kVA to 315kVA. Upgrade 1phase to 3phase R/L400m | At Scoping |  | Rukungiri
346 | HIMA MAIZE MILL | Western | Fort Portal 33 kV from Nkenda | Upgrade 200kVA 33 kV Tx to 315kVA, at Hima Maize mill. 1 additional 3 phase circuit 10 spans. | At Scoping |  | Kasese
347 | Starlight | Western | Kagadi 33 kV from Muzizi | Inject a 200 kVA transformer, construct 3 spans of Hv, 2 ccts of 3 spans LV. | At Scoping |  | Kagadi
348 | Ijumo T/C | Western | Rukungiri 33 kV from Ishaka | Upgrade from 50kVA to 100kVA only and TX wiring. | At Scoping |  | Bushenyi
349 | Kyabugimbi | Western | Ishaka 33kV from Mbarara North | inject 200kva transformer and Install MV line 1 span. 2 circuits 3 phase 4 spans each. | At Scoping |  | Bushenyi
350 | Koranorya C.O.U | Western | Lyantonde West | Inject 100kva Tx,construct h.v line eight spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
351 | Off Kilembe Rd | Western | Kasese Town 11 kV from Kasese | Injection of 100kVA, construct an HV of 2 spans, install two ccts of 3 phase, 3 spans on each circuit. | At Scoping |  | Kasese
352 | Bundibugyo PTC | Western | Bundibugyo 33 kV from Fort Portal | Inject 50 kVA and construct 3 spans of HV, 2 ccts of 3 spans LV. | At Scoping |  | Bundibugyo
353 | Haikona | Western | Kyenjojo 33 kV from Rugombe | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kyenjojo
354 | Kasojo | Western | Mpanga 2 33 kV feeder from Rugonjo | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
355 | Nyamambuka | Western | Kikorongo-Mpondwe 33 kV from Nkenda | Inject 50kVA, MV line of 400m, Reinforce from 1phase 50sqmm ACSR to 3Phase 100sqmm ACSR R/L 300m | At Scoping |  | Mpondwe
356 | Katalyeba 1 | Western | Mpanga 2 33 kV feeder from Rugonjo | Upgrade to 315 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
357 | Kacence Jomanyi tx | Western | Kakoba 11kV from Mbarara central | Injection of 100kva transformer and run 3phase for 450mtrs on both circuits | At Scoping |  | Mbarara
358 | kyamuhunga ss | Western | tea estate 11kv | Upgrade to a 100kva,upgrade single phase to 3-phase 600m and install another cct 400m | At Scoping |  | Bushenyi
359 | Mitoma TC | Western | Rukungiri 33 kV from Ishaka | inject 200kva transformer and Install MV line 1 span. 2 circuits 3 phase 5 spans each. | At Scoping |  | Bushenyi
360 | Bukonzo Mixed farm Tx | Western | Kikorongo-Mpondwe 33 kV from Nkenda | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Mpondwe
361 | Iryangabi | Western | Ibanda-Kabujjogera | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kamwenge
362 | Oil Installations | Western | Kasese Town 11 kV from Kasese | Upgrade from 200kVA to 315kVA only and add protection and tx wiring improve. | At Scoping |  | Kasese
363 | Bwera Tx 1 | Western | Kikorongo-Mpondwe 33 kV from Nkenda | Inject a 200 kVA transformer, construct 2 spans of Hv, 2 ccts of 3 spans LV. | At Scoping |  | Mpondwe
364 | Nkokonjeru 1 | Western | Ntare | Upgrade to 50kva 3phase Tx, construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
365 | Nyakasanga No.1 | Western | Kasese 33 kV from Nkenda | Inject 1*100kVA, MV (150m) install two 3 phase circuits each 300m. | At Scoping |  | Kasese
366 | nateta | Eastern | kangulumira | Inject 100kva, construct MV of 150m and improve 250m of LV 1-Phase to 2-3-phase | At Scoping |  | Kayunga
367 | Katete Rwemirinzi | Western | Kikagati | Inject 50kva Tx,construct h.v line one span and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
368 | Namulesa Ngobi family | Eastern | Mutai | Inject 200kva /11kv, extend MV by 100m and enforce LV by 300m | At Scoping |  | Jinja
369 | Bbala TC | Northern | Apac/ masindi 33kv | Construction of an MV line of route length 300m and install a 100kVA/33kV/LV transformer as an injection by tapping from Tecambia ATC tx MV terminal structure | At Scoping |  | LIRA
370 | nasenyi water pump | Eastern | Bulangira 33 kV from Iki Iki | Up grade to 200kva and new 3phase LVACSR50 R/L=300m Renforce 1phase to 3phase of RL 200m | At Scoping |  | Mbale
371 | Mubuku Mwalo | Western | Kasese 33 kV from Nkenda | Upgrade from 100kVA to 200kVA, install 1 additional 3 phase circuit 10 spans. | At Scoping |  | Kasese
372 | BUKERE P/S | Western | Mubende 33 kV from Nkonge | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kyegegwa
373 | Katete Kalugangama Village Tx | Western | Kikagati | Inject 50kva Tx,construct h.v line three spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
374 | Mubende Parents | Northern | Mubende town 11 kV from Mubende | Inject 1*200kVA. 1 span MV Toff. 2 circuits LV 1 spans each. | At Scoping |  | Mubende
375 | Budaka R | Eastern | kibuku tirinyi | upgrate to 50kva Tx, constrct lv 3phase 450m | At Scoping |  | Pallisa
376 | Warid mast -BSC | Eastern | Town | Upgrade the tx 100KVA/11kv to 200kva/11kv | At Scoping |  | Jinja
377 | Kayenje Village 2 | Northern | Kibibi 11 kV from Kiriri | Upgrade from 25kVA to 50kVA. Additional 3 phase circuit 6 spans. | At Scoping |  | Mityana
378 | Nkokonjeru C.O.U | Western | Ntare | Upgrade to 50kva 3phase Tx construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
379 | Kakindo TC | Western | Ishaka 33kV from Mbarara North | inject 200kva transformer and expand Install MV line 1 span. 2 circuits 3 phase 4 spans each. | At Scoping |  | Bushenyi
380 | Kageti T/C Tx | Western | Lyantonde West | Upgrade to 200 Kva | At Scoping |  | Mbarara
381 | Go Down 2 | Western | Kasese Town 11 kV from Kasese | Inject 1*200kVA. Install three 3 phase circuits, length 300m each. | At Scoping |  | Kasese
382 | Buremba Rd | Western | Kakoba | Inject 315kva Tx,construct h.v line three spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
383 | Dr Mugerwa | Western | Ntare | Upgrade to 50kva 3phase Tx, construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
384 | Lake Bunyonyi | Western | Kabale west | Injection of 100kva transformer, MV line of 200m and run 3phase for 450mtrs on both circuits | At Scoping |  | Kabale
385 | DR BYAMAKA TX | Western | Ntare | Upgrade to 50kva 3phase Tx, construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
386 | Kamuli Industrial Co-operatives | Eastern | Kasolwe | Upgrade the Transformer to 315kVA | At Scoping |  | Kamuli
387 | Bweyale opp soltic | Northern | Kigumba | Needs an upgrade to 100kva/33kv/Lv | At Scoping |  | Masindi
388 | bwetyaba rd | Eastern | kangulumira | Inject 200kva /11kv, extend MV by 100m and enforce LV by 350m | At Scoping |  | kayunga
389 | Naama TC | Northern | Mityana Town 11 kV from Mityana | Inject 1*100kVA. MV line of 500m, 3 phase additional 2 circuits, 10 spans. | At Scoping |  | Mityana
390 | waibale farm | Eastern | kamuli | upgrade to 50kva/33KV Three phase Tx,upgrade 1phase LV to 3phase RL- 300M using 50mmsqd ACSR | At Scoping |  | kamuli
391 | Masafu Police | Eastern | Busia | Inject 100Kva tx, Construct MV of 200m and LV line route Length 500m | At Scoping |  | Busia
392 | Rubaare lower | Western | Kabale 33kV | Construct Mv 300mt,Inject 100kVA, Upgrade Lv 300mt proposed location near Rubaare mosque | At Scoping |  | Kabale
393 | Police Station | Western | Kasese Town 11 kV from Kasese | Upgrade from 200kVA to 315kVA, add protection and tx wiring. | At Scoping |  | Kasese
394 | Kagogo Farm | Western | Ishaka 33 kV from Nkenda | Upgrade from 50kVA to 100kVA, install 1 additional 3 phase circuit, 8 spans. | At Scoping |  | Kasese
395 | St Bridget Girls 4 Miles | Western | Kikagati | Inject 50kva Tx,construct h.v line eight spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
396 | Kyera SDA | Western | Kikagati | Inject 50kva Tx,construct h.v line eight spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
397 | St Joseph Catholic Mission tx | Northern | Kitgum town 11kv from Kitgum | Injection of 100kva /33kv,extension of MV line R/L 900 mtrs,reinforcement of LV line R/L 500 mtrs | At Scoping |  | Kitgum
398 | Gombe Hospital Tx | Northern | Kibibi 11 kV from Kiriri | Inject 1*200kVA, MV (200m), reinforce LV circuit 3 phase 5 spans for each tcircuit | At Scoping |  | Mityana
399 | PURANGA TC | Northern | Kitgum 33 kV from Lira | inject 1x 50kva towards within puranga by constructing OH MVACSR 50mmsq RL400m with LV 3 phase RL 400m | At Scoping |  | Kitgum
400 | HIMA KASOJO | Western | Fort Portal 33 kV from Nkenda | Upgrade from 25kVA to 50kVA, install 2 * 3 phase circuits to replace single phase 10 spans. | At Scoping |  | Kasese
401 | KASAMBYA TC | Northern | KAKUMIRO/NDIBATA | TX injection 100kva by constructing an MV line of about 2 spans and lv improvement on two three phase ccts of about 8 spans | At Scoping |  | IGAYAZA
402 | Rwakishokye Country Club | Western | Karamurani | Inject 50kva Tx,construct h.v line two spans and construct two lv ccts of three spans 3phase @cct | At Scoping |  | Mbarara
403 | Njeru Stock Farm 2 | Eastern | Lugazi 11 kV from Njeru | Upgrade the tx 100KVA to 200kva | At Scoping |  | Jinja
404 | Kisiita A | Northern | Ndibata-Kakumiro | I propose three injections of 100KVA by constructing an MV line of 7 poles and 8 lv poles | At Scoping |  | Kisiita
405 | BURAMAGI TC | Northern | KAKUMIRO/NDIBATA | TX injection 100kva by constructing an MV line of about 8 poles and 3 spans of lv 3phase cct | At Scoping |  | IGAYAZA
406 | Nkongooro Tc | Western | Rukungiri 33 kV from Ishaka | Upgrade from 50kVA to 100kVA. LV re-inforcement of 400m | At Scoping |  | Rukungiri
407 | Mutojo T.C | Western | Ishaka Town 11 kV from Ishaka | Inject 100kVA, Install MV line 5 spans. 2 circuits 3 phase 2 spans each. | At Scoping |  | Bushenyi
408 | Mayanja Hospital | Western | Kakoba | Inject 50kva Tx,construct h.v line four spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
409 | Rweiziringiro Tc | Western | Kikagati | Inject 100kva Tx,construct h.v line one spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
410 | Rwobuyenje Village 1 | Western | Lyantonde West | Inject 50kva Tx,construct h.v line four spans and construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
411 | Kyondo Village | Western | Ishaka 33 kV from Nkenda | Upgrade to 100 kVA, reinforce 8 spans of LV 3 phase. | At Scoping |  | Kasese
412 | Buhandagazi Tc | Western | Rukungiri 33 kV from Ishaka | Inject 50KVA, MV line 400m LV line 500m | At Scoping |  | Rukungiri
413 | Ishanyu Village Tx | Western | Ishaka | Upgrade existing 50kva to 100kva,3phase Tx, construct two lv ccts of five spans 3phase @cct | At Scoping |  | Mbarara
414 | Kamdin TC | Northern | Aboke 33kv | Upgrade to 315kVA/33kv/LV transformer and conductor upgrade from ACSR 50sq mm to ACSR 100sq mm. conductor length 1000mtrs. ABC 4core 70sq mm-650mtrs | At Drawing |  | Kamdin
415 | Mwalo T.c | Western | Kasese 33 kV from Nkenda | Inject 1*100kVA transformer, MV line of 200m, install two 3 phase circuits, length 500m. | At Scoping |  | Kasese
416 | Mbatamo Village | Western | Ishaka Town 11 kV from Ishaka | Upgrade from 25kVA to 50kVA. Make toff MV, Replace single phase with 3 phase 5 spans 2 circuits. | At Scoping |  | Bushenyi
417 | St.Luke COU Bweyale | Northern | Kigumba | Ugrade to 100kVA/33kv/LV, inject existing 50kVA transformer a, extend MV line by 500m and re-inforce LV by 300m | At Scoping |  | Masindi
418 | KABARWA TC | Eastern | KUMI 33KV FEEDER | Up grade the 100kva existing tx to 200kva transformer. | At Scoping |  | Sironko
419 | MUTUFU TC | Eastern | MBALE RING 1 11KV FEEDER | Upgrade to 315kva tx with abc of 400m three phase, lv protection. | At Scoping |  | Sironko
420 | Bulonzi katwe | Northern | MUBENDE | TX injection 50kva by constructing an MV line of about 4 mv poles and 4 spans of lv network | At Scoping |  | MUBENDE
421 | Amolatar Pri School | Northern | LWALA NAMASALE | Upgrade to 315kVA, re-inforce 300m of 1phase to 3phase | At Scoping |  | Amolatar
422 | BUKWO CPS | Eastern | BUKWO 33KV FROM KERE | Upgrade to 200kva, Construction Lv 3 Phase route lrngth 500m | At Scoping |  | Bukwo
423 | UBC ODOKOMIT | Northern | NGETTA/KAMPALA ROAD | Inject a 200KVA/11KV/LV transformer, Install 11KV DOFI, Install LV protection, 6 10M LV poles, Install 6 12M MV poles including earthing. | At Scoping |  | LIRA
424 | kakila susaiti | Eastern | kamuli | inject in 50kva /33KV TX,MV extension 300m R/L,Upgrade LV from 1phase to 3phase by 200m R/L,Using 50mmsqd ACSR. | At Scoping |  | kamuli
425 | Kabwohe Centre | Western | Ishaka 11 kV from Mbarara Central | Inject 200kva/11kv/lv, construct Oh line200m, install two ccts, 3 spans on each cct | At Scoping |  | Bushenyi
426 | Abim primary | Northern | Kitgum 33kv from Lira main | Upgrade the existing one to 50kva/33kv and inject 25kva/33kv. | At Scoping |  | ABIM
427 | Kaganda Mixed Farm | Eastern | West Bank 11 kV from Nile Breweries | Upgrade the tx 100KVA to 200kva | At Scoping |  | Jinja
428 | Kamonyi village | Western | Kisoro 30kV | Construct Mv 400mt,Inject 100kVA, Upgrade Lv 250mt prosposed location near kamonyi t.c | At Scoping |  | Kisoro
429 | Kafunta TC | Eastern | Lugazi 11 kV from Njeru | Upgrade the tx 50KVA to 100kva | At Scoping |  | Jinja
430 | Bubutu TC | Eastern | Tororo 1 | Injection 100Kva, Construction MV line route Length 400m, Lv 3 phase 500m | At Scoping |  | Tororo
431 | balawoli | Eastern | kamuli | Inject 50kva /33kv TX ,upgrade 1phase LV to 3phase by 300m -RL,Extend MV by 300m R/L ,Using 50mmsqd ACSR. | At Scoping |  | kamuli
432 | Danida market | Eastern | Walukuba | Inject 200kva /11kv, extend MV by 200m and enforce LV by 400m | At Scoping |  | Jinja
433 | SOROTI ROAD NO1 | Northern | LIRA TOWN/BOROBORO | An upgrade of 200KVA to 315KVA/11KV/LV, upgrade LV protection to 250A, | At Scoping |  | LIRA
434 | Wansimba village | Eastern | Kamuli | Uprade from 50kva/33kv to 100kva/33kv and upgrade the lv line of 300m from single to 3 phase | At Scoping |  | Jinja
435 | Masindi Hotel | Northern | Nyamigisa | Injection of 200kva /11kv,extension of MV line R/L 300 mtrs,reinforcement of LV line R/L 300 mtrs and relocation of the existing 315kva/11kv at Timber factory | At Scoping |  | Masindi
436 | Nakaseeta Village | Northern | Kassanda | Inject 50kva /33kv/415v by constructing an MV network of about 6 poles and 4spans of lv one ccts of three phase | At Scoping |  | Mityana
437 | Nsambwe Village | Northern | Kibibi | Inject 50kva/ 33kv/415v by constructing an MV network of about 5 poles and 4 spans of 3 phase one lv ccts | At Scoping |  | Mityana
438 | central rd | Eastern | Mbale Ring 1 11 kV from Mbale | Upgrade to 500kva, new 3phase LVACSR100 R/L=400m Renforce 1phase to 3phase of RL 300m | At Scoping |  | Mbale
439 | Corner BELEO | Northern | LWALA NAMASALE | Inject 50KVA, extend MV by 400m and LV by 500m | At Scoping |  | Amolatar
440 | Tiira Police | Eastern | Busia | Inject 100Kva tx,Construct MV line route length 200m, Lv 3phase 500m | At Scoping |  | Tororo
441 | Walukuba Division Office | Eastern | Walukuba | Inject 200kva /11kv, extend MV by 100m and re-inforcement lv line with 200m | Document Review |  | Jinja
442 | Katikara A | Northern | Ndibata-Kakumiro | Injection of another 100kVA as the town is highly developing and has potential commercial Customers, by constructing an MV line of about 5 Mv POLES and 8lv poles | At Scoping |  | Kisiita
443 | KAYOORA1 | Northern | Kibale - Kagadi | TX injection 100kva by constructing an MV line of about 10 poles and 4 poles of lv network | At Scoping |  | Karuguuza
444 | NKONDO TC | Northern | KAKUMIRO/NDIBATA | TX injection 50kva by constructing an MV line of about 5 poles and 6 spans of lv two three phase ccts improvements | At Scoping |  | IGAYAZA
445 | District admin H/Q | Northern | MUBENDE TOWN | TX injection 100kva by constructing an MV line of about 12 poles and 8 spans of lv network on two cct 3 phase | At Scoping |  | MUBENDE
446 | Adwoko Tc | Northern | OLWENY- DOKOLO | Upgrade of 100KVA to 200KVA to cater for all the three mills in TC | At Scoping |  | Dokolo
447 | bamboo tx | Northern | kilak-abim | Injection of 200kva /33kv,extension of MV line R/L 100 mtrs,reinforcement of LV line R/L 600 mtrs | At Scoping |  | PADER
448 | Bulange TC | Eastern | JINJA INDUSTRIAL | INJECT 2X100KVA/11KV TRANSFORMERS,EXTEND MV BY 400M ON EACH,UPGRADE LV BY 400M RL ON EACH DTX | At Scoping |  | Iganga
449 | Naluwondwa TC | Northern | KAKUMIRO | TX injection 50kva by constructing MV line of about 10 poles of MV poles and about 3 spans of lv network | At Scoping |  | MUBENDE
450 | SIRONKO LOCAL GOVT H/Q | Eastern | MBALE RING 1 11KV FEEDER | Upgrade to 50kva tx, inject existing 25kVA, construct MV line of 400m with abc of 300m three phase, lv protection. | At Scoping |  | Sironko
451 | Kangulumira T/C | Northern | MUBENDE TOWN | TX injection 50kva by constructing an MV line of about 6 mv poles and 4 spans of lv network | At Scoping |  | MUBENDE
452 | IGAYAZA TC | Northern | KAKUMIRO/NDIBATA | TX injection 100kva by constructing an MV line of about 5 poles and LV line three phase improvement on two ccts of about 8 spans | At Scoping |  | IGAYAZA
453 | Katoma NWSC | Northern | MUBENDE TOWN | Relocate by constructing an mv line of about 10 MV poles and 8 spans lv 3 phase | At Scoping |  | MUBENDE
454 | bugema tc busano rd | Eastern | Bugema 11 kV from Mbale | Inject 100kva, Construct MV of 200m and Upgrade 1phase to 3phase of RL 400m | At Scoping |  | Mbale
455 | KIGULU IGANGA | Eastern | KALIRO | INJECT 2X50KVA/33KV DTX,EXTEND MV BY RL-500M and LV by 600m | At Scoping |  | Iganga
456 | BUSANJABWAKUBA | Eastern | Mbale Ring 1 11 kV from Mbale | Injection, 2*25kva, construct MV OH of RL 1.8km upgrade existing 25sqmm conductor to 50sqmm conductor of RL 800m. | At Scoping |  | Mbale
457 | NAKALOKE T/C | Eastern | Mbale Ring 1 11 kV from Mbale | Inject a 100kva, construct OH line of RL 1300m, New 3phase of RL 400m, upgrade lv 1phase ACSR25mmsq to 3phase ACSr50mmsq of RL 400m. | At Scoping |  | Mbale
458 | MASONDE | Northern | Kibale - Kagadi | TX injection 50kva by constructing MV line of about 7 poles of MV poles and about 3 spans of lv network | At Scoping |  | Karuguuza
459 | KALASA - SEMWEMA | Northern | Kibale - Kagadi | Relocation by constructing an MV line of one span ie 5 poles to take it out of line , 4 spans of three phase improvement lv one cct | At Scoping |  | Karuguuza
460 | MUROLE | Western | KISORO-KABALE 33KV | System improvement of 6 spans of ABC. | At Scoping |  | Muko
461 | NAMUNSI MALAIKA | Eastern | Mbale Ring 1 11 kV from Mbale | Inject 50kVA Tx, Construct O/H line MVACSR50 R/L=0.9km , new 3phase LVACSR50 R/L=500m Renforce 1phase to 3phase of RL 500m | At Scoping |  | Mbale
462 | NAKIGO 1 | Eastern | BUGIRI | INJECT 50KVA/33KV TX,UPGRADE LV BY 400M RL,MV BY 300M | At Scoping |  | Iganga
463 | BULUGENI TC | Eastern | KAPCHORWA 33KV FEEDER | Tx injection of 100Kva tx with 10*10m poles, 400m*abc 3 phase. | At Scoping |  | Sironko
464 | East Acholi Cooperatives tx | Northern | Kitgum town 11kv from Kitgum | Injection of 200kva /11kv,extension of MV line R/L 900 mtrs,reinforcement of LV line R/L 500 mtrs | At Scoping |  | KITGUM
465 | Mourita | Eastern | Nakapiripirit 33kv@Moroto | Upgrading the Tx to 50kVA, inject existing 25kVA, construct MV line of 500m and reinforce LV of 600m | At Scoping |  | Nakapiripirit
466 | Bukoloto Road | Eastern | kangulumira | Inject a 100kVA Transformer, extend MV by 200m and LV by 500m | At Scoping |  | Kayunga
467 | Kigolobya Tc | Northern | Hoima Town 11kv | Inject 50kva/11kv/415v along kyabisagazi road by construction of one span of MV line ie about 4 mv poles and costruct one lv cct of about 3 spans 3 phase | At Scoping |  | Hoima